## R
ta File Name: D:\LT | LTrafoDesign_v6100\R | rtVB.dat
* Using Standard Da | ta from Files ***
TE: 2021.11.10 |  | IQUID TYPE TRANSFOR | MER CALCULATION (Ver | n 6.10.0) |  | Time: 14:03:54
DER : 100033415 | DESIGN: Data Set 1 | ENGINEER: LASINDU | CUSTOMER NAME | DCO
A - 1000 Liquid | Type ONAN Cooli | 55 C Rise Th | ree Phase 50 Hz | Style Number: Non | e
: 33000 + 2- 2x 2. | 50 % TC: Off-load T | Changer | BIL: 170 (Delt | Line/Coil Amps: |  | 17.495/ 10.101
: 415 |  |  | BIL: 3 (Wye | Line/Coil Amps: | 1 | 391.205/1391.205
------------------- | -------------------- | ----- S T A C K E D | C O R E -------- | --------- Width -- |  | Build ----- Weight -
Core Design.......: | OVAL Mitered | Diagonal Dimension: | 190.000 x 281.863 mm | Step 1: 190.000, |  | 91.863 mm 673.1 kg
Grade/Frame Type..: | 23ZDKH / 3-Leg | Window Height.....: | 867.000 mm | Step 2: 180.000, |  | 61.410 mm 426.3 kg
INDUCTION.........: | 1.700 Tesla | Center to Center..: | 513.042 mm | Step 3: 160.000, |  | 41.400 mm 255.5 kg
VPT, W/kg, PBase..: | 14.975, 0.876, 0.77 | Gross/Net CSA.....: | 410.3 / 396.8 cm2 | Step 4: 140.000, |  | 25.990 mm 140.3 kg
100 % Exc Current.: | 0.8276 | Weight of Core-Leg: | 936.9 kg | Step 5: 120.000, |  | 18.860 mm 87.3 kg
Sound/Natural Freq: | 55.0 db / 402 Hz | Weight of Yoke....: | 595.6 kg | Step 6: 0.000, |  | 0.000 mm 0.0 kg
Peak HV Inrush Cur: | 195 amp | Core Net Weight...: | 1532.5 kg | Step 7: 0.000, |  | 0.000 mm 0.0 kg
Utilization Factor: | 0.8958 | Core Scrap Weight.: | 49.9 kg | Step 8: 0.000, |  | 0.000 mm 0.0 kg
Standard Core No..: | NONE STANDARD | Core Gross Weight.: | 1582.4 kg | Step 9: 0.000, |  | 0.000 mm 0.0 kg
Ovality Factor....: | 1.261 | Use Max Steel Wi | dth (Steps minus 1) | Using Std | S | teel Widths
Core Perimeter....: | 780.6 mm | Delta Build.......: | 91.9 mm
------------------- | -------------------- | L O W V O L T A | G E W I N D I N G | ------------------ | - | --------------------
Type of Coil......: | AL-Foil | Coil-Length.......: | 840.000 mm | ELECT LENGTH...... | : | 800.000 mm
TURNS PER COIL....: | 1 x 16.0 | Inside Dimensions.: | 196.000 x287.863 mm | Strip-#x#x Wd x Tk | : | 1x2x 800.00 x 0.800
CURRENT DENSITY...: | 1.087 A/mm2 | Outside Dimensions: | 272.065 x363.928 mm | Cond/Lead Weight.. | : | 152.44 / 17.07 kg
|  | Inner Perimeter...: | 799.5 mm
Cooling Ducts Tk/#: | 4.500 mm / 1.00 | Rad Blds (H,Leg,L): | 38.03/ 38.03/ 38.03 | Lay/Trn/Duc Wts... | : | 15.20/ 0.00/ 1.36
Eff No Cool Ducts.: | HV: 1 Leg: 1 LV: 1 | Axial Allowance...: | 0.000 mm | Total Insul Weight | : | 16.56 kg
Short-Circuit Curr: | 66191 Amp. | Num Support Sticks: | 12
Mean Turn Length..: | 918.961 mm | Lead: Wd / Tk..: | 100.000 / 10.000 mm | Total Coil Weight. | : | 186.07 kg
Max Turn Lth Buckl: | 3716.440 mm | Bus Bar: Wd / Tk..: | 100.000 / 10.000 mm
|  | Layer Insul Tk....: | 0.350 mm
T-RISE/GRADIENT...: | 37.5/ 8.7 deg C | Watts/sq m .......: | 358.363 | Resistance (Coil). | : | 0.000398 @ 75 C
Turn CSA .........: | 1280.000 mm2 |  |  | Conductor Dims.... | : | Specified Size
------------------- | -------------------- | I G H V O L T A | G E W I N D I N G | ------------------ | - | --------------------
Type of Coil......: | Layer-Wound Coil | Coil-Length.......: | 840.000 mm | Cond Mec/Elec Lgth | : | 750.000 / 743.780
Conductor.........: | AL-Round | Inside Dimensions.: | 310.065 x 401.928 | Cond-Dim Per Turn. | : | 1x2x 3.000 x 3.000
Turns Tot./Nominal: | 2314/ 2204 | Outside Dimensions: | 488.042 x 579.905 | Cond Area Per Turn | : | 14.13717 mm2
Cooling Ducts Tk/#: | 4.500 mm / 1.00 | Rad Blds (H,Leg,L): | 88.99/ 88.99/ 88.99 | HV Conductor Wt... | : | 380.88 kg
Eff No Cool Ducts.: | HV: 1 Leg: 1 LV: 1 | Add Rad Allowance.: | 0.000 mm | Lay/Trn/Duc Wts... | : | 55.01/ 0.00/ 2.12
Mean Turn Length..: | 1437.4 mm | Layer/Turn Ins Bd.: | 0.675/ 0.110 mm | Insulation Weight. | : | 57.14 kg
LayIns Tk.........: | (18 Full) 0.675 mm | LayIns RB W/OvBld.: | 13.81 mm | Average LayIns Tk. | : | 0.675 mm
CURRENT DENSITY...: | 0.715 A/mm2 | # Sup Pts/Ax All..: | 12 / 0.000 mm | Total Coil Weight. | : | 438.01 kg
# Lay: Max/Min tpl: | 20# 120.00/ 34.00 * | Axial Sections....: | 1 | Layer-Layer Volts. | : | 3581.4
T-RISE/GRADIENT...: | 36.0/ 7.2 deg C | Watts/sq m .......: | 222.534 | Resistance (Coil). | : | 7.7580 @ 75 C
|  |  |  | Conductor Dims.... | : | Standard Size
------------------- | -------------------- | L E C T R I C A L | C L E A R A N C E | ------------------ | - | --------------------
LV to Core Leg(mm): | 3.00x 3.00x 7.00 | LV Cond to Yoke...: | 33.500 mm | Total HV-LV Offset | : | 50.000 mm
Eff Hi-Lo ElecSpan: | 19.000 mm | Ph-Ph Elec Spacing: | 25.000 mm | Max LV Sup Span... | : | 39.000 mm
HV-HSide/HV-LSide.: | 55.00 / 55.00 mm | HV-Ends...........: | 55.000 mm | Yoke-Case Top/Bot. | : | 220.00 / 40.00 mm
HV Fixed Gap......: | 0.000 mm
-------- BASIS FOR | CALCULATIONS ------- | ------------------- | -- MATERIAL PRICES | USD/KG (17-08-01 | ) | -------------------
Netw.Short Cir.Cap: | 1000.0 MVA | E Rnd Wire: AL/CU.: | 4.56 / 11.73 | Core Cost......... | : | 3.88
Wdg Rise Limit....: | 55.0 deg C | Rect Wire : Al/Cu.: | 5.63 / 7.37 | Turn/Lay/DD Insul. | : | 2.18 / 3.28 / 4.1
Top Oil Rise Limit: | 50.0 deg C | Foil Cond: AL/CU..: | 3.59 / 11.73 | Mineral/Silicone.. | : | 0.98 / 6.12
Per/watt No Ld/Ld.: | 6.33 / 2.04 | LME/1000 (CU/AL)..: | 0 / 0 | Case Steel/Cooling | : | 0.78 / 1.71
------------------- | -------------------- | WEIGHTS, DIMENSIONS | , AND COOLING (RIBS) | ------------------ | - | --------------------
Active Part Weight: | 2192 kg |  |  | C&C Dim: Ht/Lgth.. | : | 1247.00/1514.13 mm
Clamp & Brace Wt..: | 219 kg | H-L Barrier Weight: | 35.54 kg
Mineral Oil Weight: | 1202 kg | Ribs-Press/Weight.: | 0.17 kp/cm2 386 | Rib Height:1,2,3,4 | : | 1300/1300/1300/1300
Bus bar/TC Weight.: | 8/ 0 kg | Rib Pitch: 1,2,3,4: | 100/ 70/ 100/ 70 | No of Ribs:1,2,3,4 | : | 16/ 10/ 16/ 10
Cov/Case & Cooling: | 74/ 471 kg | Rib Depth: 1,2,3,4: | 260/ 100/ 260/ 100 | Rib Pan Wd:1,2,3,4 | : | 1624/ 730/1624/ 730
Total Weight......: | 4166 kg | Rib Thick: 1,2,3,4: | 1.50/1.50/1.50/1.50 | Case: Lt/Wd/Ht(mm) | : | 1624.1x 730.0x1507.0
------------------- | -------------------- | ------PRICE & COST | IN USD UNITS ------- | ------------------ | - | --------------------
Core Cost.........: | 5946 | HV / LV Coil Cost.: | 2013/ 680 | Labor & VOH/Hours. | : | 0 / 0
Case/Cooling Cost.: | 66/ 658 | Bracing Cost......: | 171 | Design Matl-Cost.. | : | 11295
Mineral Oil.......: | 1177 | Assy and Misc.....: | 583 | Variable Cost..... | : | 11295
EVALUATED LOSSES..: | 19762 | EVALUATED COST....: | 31057 | RECOMMENDED PRICE. | : | 22589
------------------- | -------------------- | ---------- PERFORMA | NCE DATA ----------- | ------------------ | - | --------------------
HV Wdg DC Losses..: | 2375 Watts | LV Wdg DC Losses..: | 2309 Watts
HV Watts (% Eddy).: | 2530 ( 6.1) | LV Watts (% Eddy).: | 2529 ( 4.3) | LV Bus Bar / Stray | : | 192 / 270
No Load Losses....: | 1343 Watts | Tot-Ld Watts(%Ed).: | 5521 (13.1) | Total Losses(ONAN) | : | 6864 @ 75 C
% X / % R / % Lead: | 4.86/0.55/0.08 % | % Z (HV-LV-Lead)..: | 4.968 % | TOP OIL RISE...... | : | 36.0 deg C
|  | % Z Guaranteed....: | 5.000 %
------------------- | -------------------- | ------------------- | -------------------- | ------------------ | - | --------------------
TES: HV Axial & Ra | d Factors - 1.000, | 880 LV Rad Fact | or - 0.920 OPT | : (Min Evaluated C | o | st )
MARG/MULT.: < | Rise>: Top Oil= 0 H | 0 L= 0 T= 0 <Loss | >: Core= 1.000 BusB= | 1.0 Eddy H= 1.0 | L | = 1.0 Stray= 1.0
CORE: Std(NO | ) Wds(YES) C-C(NO ) | g(NO ), COND: Foil | Tk(NO ), CLEAR: Wd | O ), CASE: Std(NO |  | ) CALC: Sh Cir(YES)
Circuit Load | Factors: HV= 1.000, | LV= 1.000, TV= 1. | 000
Circuit Load | Factors: HV= 1.000, | LV= 1.000, TV= 1. | 000
Using LTL Cor | e Loss Calculation T | nical Standard: < N | O >
Using LTL Loa | d Loss Calculation T | nical Standard: < N | O >
Impedance Mod | el: Convensional
Tapping Turns | @.......: 1 - 2314, | - 2259, 3 - 2204, 4 | - 2149, 5 - 2094

## P
| Section | Value | Row No | Column No
| Start | DESIGN: Data Set 1 | 7 | 2
| Core | C O R E -------- | 10 | 4
| LV | L O W V O L T A | 21 | 3
| HV | I G H V O L T A | 33 | 3
| Clearances | L E C T R I C A L | 44 | 3
| Calculations | CALCULATIONS ------- | 48 | 2
| Weights & Dimensions | WEIGHTS, DIMENSIONS | 15 | 3
| Prices | IN USD UNITS ------- | 58 | 4
| Performance data | NCE DATA ----------- | 62 | 4
| Factors | -------------------- | 67 | 4
Start | 0 | 1 | 2 | 3 | 4 | 5 | 6
-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-1 | TE: 2021.11.10 | 0 | IQUID TYPE TRANSFOR | MER CALCULATION (Ver | n 6.10.0) | 0 | Time: 14:03:54
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | DER : 100033415 | DESIGN: Data Set 1 | ENGINEER: LASINDU | CUSTOMER NAME | DCO | 0 | 0
2 | A - 1000 Liquid | Type ONAN Cooli | 55 C Rise Th | ree Phase 50 Hz | Style Number: Non | e | 0
3 | : 33000 + 2- 2x 2. | 50 % TC: Off-load T | Changer | BIL: 170 (Delt | Line/Coil Amps: | 0 | 17.495/ 10.101
4 | : 415 | 0 | 0 | BIL: 3 (Wye | Line/Coil Amps: | 1 | 391.205/1391.205
5 | ------------------- | -------------------- | ----- S T A C K E D | C O R E -------- | --------- Width -- | 0 | Build ----- Weight -
6 | Core Design.......: | OVAL Mitered | Diagonal Dimension: | 190.000 x 281.863 mm | Step 1: 190.000, | 0 | 91.863 mm 673.1 kg
Core
0 | ------------------- | -------------------- | ----- S T A C K E D | C O R E -------- | --------- Width -- | 0 | Build ----- Weight -
1 | Core Design.......: | OVAL Mitered | Diagonal Dimension: | 190.000 x 281.863 mm | Step 1: 190.000, | 0 | 91.863 mm 673.1 kg
2 | Grade/Frame Type..: | 23ZDKH / 3-Leg | Window Height.....: | 867.000 mm | Step 2: 180.000, | 0 | 61.410 mm 426.3 kg
3 | INDUCTION.........: | 1.700 Tesla | Center to Center..: | 513.042 mm | Step 3: 160.000, | 0 | 41.400 mm 255.5 kg
4 | VPT, W/kg, PBase..: | 14.975, 0.876, 0.77 | Gross/Net CSA.....: | 410.3 / 396.8 cm2 | Step 4: 140.000, | 0 | 25.990 mm 140.3 kg
5 | 100 % Exc Current.: | 0.8276 | Weight of Core-Leg: | 936.9 kg | Step 5: 120.000, | 0 | 18.860 mm 87.3 kg
6 | Sound/Natural Freq: | 55.0 db / 402 Hz | Weight of Yoke....: | 595.6 kg | Step 6: 0.000, | 0 | 0.000 mm 0.0 kg
7 | Peak HV Inrush Cur: | 195 amp | Core Net Weight...: | 1532.5 kg | Step 7: 0.000, | 0 | 0.000 mm 0.0 kg
8 | Utilization Factor: | 0.8958 | Core Scrap Weight.: | 49.9 kg | Step 8: 0.000, | 0 | 0.000 mm 0.0 kg
9 | Standard Core No..: | NONE STANDARD | Core Gross Weight.: | 1582.4 kg | Step 9: 0.000, | 0 | 0.000 mm 0.0 kg
10 | Ovality Factor....: | 1.261 | Use Max Steel Wi | dth (Steps minus 1) | Using Std | S | teel Widths
11 | Core Perimeter....: | 780.6 mm | Delta Build.......: | 91.9 mm | 0 | 0 | 0
12 | ------------------- | -------------------- | L O W V O L T A | G E W I N D I N G | ------------------ | - | --------------------
13 | Type of Coil......: | AL-Foil | Coil-Length.......: | 840.000 mm | ELECT LENGTH...... | : | 800.000 mm
14 | TURNS PER COIL....: | 1 x 16.0 | Inside Dimensions.: | 196.000 x287.863 mm | Strip-#x#x Wd x Tk | : | 1x2x 800.00 x 0.800
LV
1 | ------------------- | -------------------- | L O W V O L T A | G E W I N D I N G | ------------------ | - | --------------------
2 | Type of Coil......: | AL-Foil | Coil-Length.......: | 840.000 mm | ELECT LENGTH...... | : | 800.000 mm
3 | TURNS PER COIL....: | 1 x 16.0 | Inside Dimensions.: | 196.000 x287.863 mm | Strip-#x#x Wd x Tk | : | 1x2x 800.00 x 0.800
4 | CURRENT DENSITY...: | 1.087 A/mm2 | Outside Dimensions: | 272.065 x363.928 mm | Cond/Lead Weight.. | : | 152.44 / 17.07 kg
5 | 0 | 0 | Inner Perimeter...: | 799.5 mm | 0 | 0 | 0
6 | Cooling Ducts Tk/#: | 4.500 mm / 1.00 | Rad Blds (H,Leg,L): | 38.03/ 38.03/ 38.03 | Lay/Trn/Duc Wts... | : | 15.20/ 0.00/ 1.36
7 | Eff No Cool Ducts.: | HV: 1 Leg: 1 LV: 1 | Axial Allowance...: | 0.000 mm | Total Insul Weight | : | 16.56 kg
8 | Short-Circuit Curr: | 66191 Amp. | Num Support Sticks: | 12 | 0 | 0 | 0
9 | Mean Turn Length..: | 918.961 mm | Lead: Wd / Tk..: | 100.000 / 10.000 mm | Total Coil Weight. | : | 186.07 kg
10 | Max Turn Lth Buckl: | 3716.440 mm | Bus Bar: Wd / Tk..: | 100.000 / 10.000 mm | 0 | 0 | 0
11 | 0 | 0 | Layer Insul Tk....: | 0.350 mm | 0 | 0 | 0
12 | T-RISE/GRADIENT...: | 37.5/ 8.7 deg C | Watts/sq m .......: | 358.363 | Resistance (Coil). | : | 0.000398 @ 75 C
13 | Turn CSA .........: | 1280.000 mm2 | 0 | 0 | Conductor Dims.... | : | Specified Size
HV
2 | ------------------- | -------------------- | I G H V O L T A | G E W I N D I N G | ------------------ | - | --------------------
3 | Type of Coil......: | Layer-Wound Coil | Coil-Length.......: | 840.000 mm | Cond Mec/Elec Lgth | : | 750.000 / 743.780
4 | Conductor.........: | AL-Round | Inside Dimensions.: | 310.065 x 401.928 | Cond-Dim Per Turn. | : | 1x2x 3.000 x 3.000
5 | Turns Tot./Nominal: | 2314/ 2204 | Outside Dimensions: | 488.042 x 579.905 | Cond Area Per Turn | : | 14.13717 mm2
6 | Cooling Ducts Tk/#: | 4.500 mm / 1.00 | Rad Blds (H,Leg,L): | 88.99/ 88.99/ 88.99 | HV Conductor Wt... | : | 380.88 kg
7 | Eff No Cool Ducts.: | HV: 1 Leg: 1 LV: 1 | Add Rad Allowance.: | 0.000 mm | Lay/Trn/Duc Wts... | : | 55.01/ 0.00/ 2.12
8 | Mean Turn Length..: | 1437.4 mm | Layer/Turn Ins Bd.: | 0.675/ 0.110 mm | Insulation Weight. | : | 57.14 kg
9 | LayIns Tk.........: | (18 Full) 0.675 mm | LayIns RB W/OvBld.: | 13.81 mm | Average LayIns Tk. | : | 0.675 mm
10 | CURRENT DENSITY...: | 0.715 A/mm2 | # Sup Pts/Ax All..: | 12 / 0.000 mm | Total Coil Weight. | : | 438.01 kg
11 | # Lay: Max/Min tpl: | 20# 120.00/ 34.00 * | Axial Sections....: | 1 | Layer-Layer Volts. | : | 3581.4
12 | T-RISE/GRADIENT...: | 36.0/ 7.2 deg C | Watts/sq m .......: | 222.534 | Resistance (Coil). | : | 7.7580 @ 75 C
13 | 0 | 0 | 0 | 0 | Conductor Dims.... | : | Standard Size
14 | ------------------- | -------------------- | L E C T R I C A L | C L E A R A N C E | ------------------ | - | --------------------
Clearances
3 | ------------------- | -------------------- | L E C T R I C A L | C L E A R A N C E | ------------------ | - | --------------------
4 | LV to Core Leg(mm): | 3.00x 3.00x 7.00 | LV Cond to Yoke...: | 33.500 mm | Total HV-LV Offset | : | 50.000 mm
5 | Eff Hi-Lo ElecSpan: | 19.000 mm | Ph-Ph Elec Spacing: | 25.000 mm | Max LV Sup Span... | : | 39.000 mm
6 | HV-HSide/HV-LSide.: | 55.00 / 55.00 mm | HV-Ends...........: | 55.000 mm | Yoke-Case Top/Bot. | : | 220.00 / 40.00 mm
7 | HV Fixed Gap......: | 0.000 mm | 0 | 0 | 0 | 0 | 0
8 | -------- BASIS FOR | CALCULATIONS ------- | ------------------- | -- MATERIAL PRICES | USD/KG (17-08-01 | ) | -------------------
9 | Netw.Short Cir.Cap: | 1000.0 MVA | E Rnd Wire: AL/CU.: | 4.56 / 11.73 | Core Cost......... | : | 3.88
10 | Wdg Rise Limit....: | 55.0 deg C | Rect Wire : Al/Cu.: | 5.63 / 7.37 | Turn/Lay/DD Insul. | : | 2.18 / 3.28 / 4.1
Calculations
4 | -------- BASIS FOR | CALCULATIONS ------- | ------------------- | -- MATERIAL PRICES | USD/KG (17-08-01 | ) | -------------------
5 | Netw.Short Cir.Cap: | 1000.0 MVA | E Rnd Wire: AL/CU.: | 4.56 / 11.73 | Core Cost......... | : | 3.88
6 | Wdg Rise Limit....: | 55.0 deg C | Rect Wire : Al/Cu.: | 5.63 / 7.37 | Turn/Lay/DD Insul. | : | 2.18 / 3.28 / 4.1
7 | Top Oil Rise Limit: | 50.0 deg C | Foil Cond: AL/CU..: | 3.59 / 11.73 | Mineral/Silicone.. | : | 0.98 / 6.12
8 | Per/watt No Ld/Ld.: | 6.33 / 2.04 | LME/1000 (CU/AL)..: | 0 / 0 | Case Steel/Cooling | : | 0.78 / 1.71
9 | ------------------- | -------------------- | WEIGHTS, DIMENSIONS | , AND COOLING (RIBS) | ------------------ | - | --------------------
10 | Active Part Weight: | 2192 kg | 0 | 0 | C&C Dim: Ht/Lgth.. | : | 1247.00/1514.13 mm
11 | Clamp & Brace Wt..: | 219 kg | H-L Barrier Weight: | 35.54 kg | 0 | 0 | 0
Weights & Dimensions
-1 | ------------------- | -------------------- | WEIGHTS, DIMENSIONS | , AND COOLING (RIBS) | ------------------ | - | --------------------
0 | Active Part Weight: | 2192 kg | 0 | 0 | C&C Dim: Ht/Lgth.. | : | 1247.00/1514.13 mm
1 | Clamp & Brace Wt..: | 219 kg | H-L Barrier Weight: | 35.54 kg | 0 | 0 | 0
2 | Mineral Oil Weight: | 1202 kg | Ribs-Press/Weight.: | 0.17 kp/cm2 386 | Rib Height:1,2,3,4 | : | 1300/1300/1300/1300
3 | Bus bar/TC Weight.: | 8/ 0 kg | Rib Pitch: 1,2,3,4: | 100/ 70/ 100/ 70 | No of Ribs:1,2,3,4 | : | 16/ 10/ 16/ 10
4 | Cov/Case & Cooling: | 74/ 471 kg | Rib Depth: 1,2,3,4: | 260/ 100/ 260/ 100 | Rib Pan Wd:1,2,3,4 | : | 1624/ 730/1624/ 730
5 | Total Weight......: | 4166 kg | Rib Thick: 1,2,3,4: | 1.50/1.50/1.50/1.50 | Case: Lt/Wd/Ht(mm) | : | 1624.1x 730.0x1507.0
6 | ------------------- | -------------------- | ------PRICE & COST | IN USD UNITS ------- | ------------------ | - | --------------------
7 | Core Cost.........: | 5946 | HV / LV Coil Cost.: | 2013/ 680 | Labor & VOH/Hours. | : | 0 / 0
8 | Case/Cooling Cost.: | 66/ 658 | Bracing Cost......: | 171 | Design Matl-Cost.. | : | 11295
Prices
6 | ------------------- | -------------------- | ------PRICE & COST | IN USD UNITS ------- | ------------------ | - | --------------------
7 | Core Cost.........: | 5946 | HV / LV Coil Cost.: | 2013/ 680 | Labor & VOH/Hours. | : | 0 / 0
8 | Case/Cooling Cost.: | 66/ 658 | Bracing Cost......: | 171 | Design Matl-Cost.. | : | 11295
9 | Mineral Oil.......: | 1177 | Assy and Misc.....: | 583 | Variable Cost..... | : | 11295
10 | EVALUATED LOSSES..: | 19762 | EVALUATED COST....: | 31057 | RECOMMENDED PRICE. | : | 22589
11 | ------------------- | -------------------- | ---------- PERFORMA | NCE DATA ----------- | ------------------ | - | --------------------
12 | HV Wdg DC Losses..: | 2375 Watts | LV Wdg DC Losses..: | 2309 Watts | 0 | 0 | 0
13 | HV Watts (% Eddy).: | 2530 ( 6.1) | LV Watts (% Eddy).: | 2529 ( 4.3) | LV Bus Bar / Stray | : | 192 / 270
Performance data
7 | ------------------- | -------------------- | ---------- PERFORMA | NCE DATA ----------- | ------------------ | - | --------------------
8 | HV Wdg DC Losses..: | 2375 Watts | LV Wdg DC Losses..: | 2309 Watts | 0 | 0 | 0
9 | HV Watts (% Eddy).: | 2530 ( 6.1) | LV Watts (% Eddy).: | 2529 ( 4.3) | LV Bus Bar / Stray | : | 192 / 270
10 | No Load Losses....: | 1343 Watts | Tot-Ld Watts(%Ed).: | 5521 (13.1) | Total Losses(ONAN) | : | 6864 @ 75 C
11 | % X / % R / % Lead: | 4.86/0.55/0.08 % | % Z (HV-LV-Lead)..: | 4.968 % | TOP OIL RISE...... | : | 36.0 deg C
12 | 0 | 0 | % Z Guaranteed....: | 5.000 % | 0 | 0 | 0
13 | ------------------- | -------------------- | ------------------- | -------------------- | ------------------ | - | --------------------
Factors
8 | ------------------- | -------------------- | ------------------- | -------------------- | ------------------ | - | --------------------
9 | TES: HV Axial & Ra | d Factors - 1.000, | 880 LV Rad Fact | or - 0.920 OPT | : (Min Evaluated C | o | st )
10 | MARG/MULT.: < | Rise>: Top Oil= 0 H | 0 L= 0 T= 0 <Loss | >: Core= 1.000 BusB= | 1.0 Eddy H= 1.0 | L | = 1.0 Stray= 1.0
11 | CORE: Std(NO | ) Wds(YES) C-C(NO ) | g(NO ), COND: Foil | Tk(NO ), CLEAR: Wd | O ), CASE: Std(NO | 0 | ) CALC: Sh Cir(YES)
12 | Circuit Load | Factors: HV= 1.000, | LV= 1.000, TV= 1. | 000 | 0 | 0 | 0
13 | Circuit Load | Factors: HV= 1.000, | LV= 1.000, TV= 1. | 000 | 0 | 0 | 0
14 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | Using LTL Cor | e Loss Calculation T | nical Standard: < N | O > | 0 | 0 | 0
16 | Using LTL Loa | d Loss Calculation T | nical Standard: < N | O > | 0 | 0 | 0
17 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Q
MARGINS
Core Loss | 10
Cu Loss | 10
No Load Current | 30
Total Weight | 100
Material Name in MM | Margin (%)
Fin Radiators | 0 | 0 |  | 2.5
| 0 | 0 |  | 2.5
Panel Type Radiators | 0 | 0 |  | 2.5 |  |  | Removable
Cover+Base+Flange | 0 | 0 |  | 2.5
Steel (Total) | 0 | 0 |  | 2.5
Wooden Total | 0 | 0 |  | 2.5
Core steel | 0 | 0 |  | 2.5
Oil | 0 | 0 |  | 2.5
Copper Foil | 0 | 0 |  | 2.5
Round Copper | 0 | 0 |  | 2.5
Copper Bus Bar | 0 | 0 |  | 2.5
Rectangular Copper | 0 | 0 |  | 2.5
DDP-Double Layer | 0 | 0 |  | 2.5
0.15 DDP-Single Layer | 0 | 0 |  | 2.5
0.25 DDP-Single Layer | 0 | 0 |  | 2.5
Strip Insulation | 0 | 0 |  | 2.5
Corrugator Boards- 9.0x2.0 mm | 0 | 0 |  | 2.5
LV Strip | 0 | 0 |  | 2.5
HV Strip | 0 | 0 |  | 2.5
Galvanizing | 0 | 0 |  | 2.5
Primer Paint & Thinner | 0 | 0 |  | 2.5
Powder Paint | 0 | 0 |  | 2.5
Rectangular Copper
ELECTRICAL DATA
TYPE | Fin Radiator |  |  | Ribs | Ribs-Press/Weight.:
| Hermetically Sealed |  |  | 0 | 0
| N | N
Hermetically Sealed
Conservator Type
Fin Radiator
Panel type
Y
N
kVA | 1000 | 3 | 13 |  |  |  |  | Tap Wire | Area | Ph density | Line Density | ph (kg) | line (kg)
HV VOLTS | 33000 | 1 | 9 | 18 |  |  |  | 3 | 7.0686 | 1.429 | 2.475 | 6 | 2
LV VOLTS | 415 | 1 | 7 |  |  |  |  | 7/1.7 | 15.8886 | 0.63574 | 1.1011 | 0 | 0
LV Coil current | 1391.205 | 8 | 16 | 391.205/1391.205 |  | 1 | 2 | 19/1.35 | 27.1964 | 0.37141 | 0.64328 | 0 | 0
LV line current | 1391.205 | [6 empty] | Choise |  | 1.429 | 2.475
LV Coil current density | 1.087 | 7
: 33000 + 2- 2x 2. | [7 empty] | Capacity | Tapping | Barrier DDP
HV coil current | 10.101 | 14 | 8 | 17.495/ 10.101 |  | Closest capacity | 1000 | 100 | 3 | 0.5
HV line current | 17.495 |  |  |  |  | Tapping Weight | 6 | 160 | 3 | 0.5
[8 empty] | 250 | 4 | 0.75
HV voltage (kV) | 33 | [6 empty] | 400 | 4 | 1
Basic Insulation Level | 170 | 4 | 10 |  |  |  |  | 630 | 5 | 1.5
%X | 4.86 | 16 | 10 | 5 | 4.86/0.55/0.08 % | % X / % R / % Lead: |  | 800 | 5 | 2
%R | 0.55 | [6 empty] | 1000 | 6 | 2.5
Frequency | 50 | 5 | 18 |  |  |  |  | 1250 | 6 | 3.5
Phases | 3 | ree | [5 empty] | 1600 | 7 | 4.5
Tappings |  | 9 | 12 | 18 |  |  |  | 2000 | 7 | 5.5
+ | 2 | [6 empty] | 2500 | 8 | 6.5
- | -2 | 2 | [5 empty] | 3150 | 13 | 7.5
Steps | 2.5 | 4 | 5
| 5% | 2 | 1
| 2.5% | 1 | 2
| 0% | 0 | 3
| -2.5% | -1 | 4
| -5% | -2 | 5
| - | 0
| - | 0
| - | 0
| - | 0
Vector Group
LV | yn |  | yn
HV | D |  | D
Dyn
Dyn11
Temp. Rise Windings | 55 | 11 | 55
Temp. Rise Top oil | 50 | 10 | 50
% impedence | 4.97 | 4.968 % | % Z (HV-LV-Lead)..: |  | 4.968 | 4.968
Full Load Loss | 2.04 | 1.1 | 2529 |  |  | 2.04
No Load Loss | 6.33 | 1.1 | #VALUE! | #VALUE! |  | 6.33 |  |  | 4.9616 | 0.2529
No load Current | 0.8276
Sound level | 55
Core Loss Factor | 1 | 16 | 8
Factor k x sqrt(2) | #VALUE! | #VALUE! | #VALUE!
kVA | % Z | % Z-pu | FL loss | NL loss | PU load | PF | X | sin X | %X | %R | %FE | %Eff | %Reg
1000 | 4.97 | 4.97 | 2.04 | 6.33 | 1 | 0.8 | 0.6435 | 0.6 | 4.97 | 0.000204 | 0.000633 | 99.999 | 3.0612
DIMENSIONS
CASE
Case-Length | 1624 | 14 | 7 | 20
Case-Width | 730
Case-Height | 1507
HEIGHTS |  | WEIGHTS
Conservator | 0 | 0
HV Box | 0 | 0
ISD | 290 | 5
Plug-in Type 36 kV 250 A Interface B | 150 | 15
EN 2000 | 240 | 24.96
LV Box | 0 | 0
Height for base skid and cover | 110 | 91.0846
CABLE BOX
No of intakes /Phase (LV) | 4
LV Box Depth | 0 |  |  | Conservator Length | 0
LV Box Width | 0 |  |  | Panel Add. to Length | 0
HV Box Depth | 0 |  |  | Panel Add. to Width | 0
HV Box Width | 0
WTI Box Depth | 0
Tolerance
Length | 1844 | 20 | 1824
Width | 1270 | 20 | 1250
Height | 1927 | 20 | 1907
Weight-TOTAL | 4360 | 50 | 4302
Weight-OIL | 1210 |  | 1210
Weight-ACTIVE PART | 2200 |  | 2192
Weight-Untanking | 2360 | 50 | 2306
Container Arrangement |  | 40' |  |  | 20'
Length |  | 12045 |  |  | 5919
Width |  | 2280 |  |  | 2286
Weight | 100 | 27396 |  |  | 22100
Length/Length |  | 6 | 1 |  | 3 | 1
Length/Width |  | 9 | 1 |  | 4 | 1
Weight | 6 | 6 |  | 4 | 4
DESIGN
Design | 100033415 |  |  | DER : 100033415
Date | 2021.11.10 | 5 | 6 | Time: 14:03:54 | IQUID TYPE TRANSFOR |  |  | TE: 2021.11.10
Time | 14:03:54 | [6 empty] | 3
Customer | DCO
WINDING DATA
Coil Length | 840 | 838 | 750 | 743.78 | 800 | 0 | 1
Window height | 867 | 867.000 | 9
Center to center | 513 | 513.042 | 9
Core Type | OVAL
Height from yoke to cover | 220 | 40.00 mm | 40
LV layer insulations thickness | 0.35
INSULATION
LV layer insulations thickness | 0.35 | 0.35 | 15.2 | 100.000 | 0.350
838mm x 0.15 DDP DL | 0 | 0 |  |  |  | 0.15 DDP | 0.25 DDP | 0.15 DDP | 0.25 DDP
838mm x 0.15 DDP SL | 0 | 0 |  |  | 0.15 | 1 |  | 1
838mm x 0.25 DDP SL | 15.2 | 1 |  |  | 0.18 | 1 |  | 1
[5 empty] | 0.25 | 1 |  | 1
[5 empty] | 0.3 | 1 |  | 2
HV layer insulations thickness | 0.7 | 0.675 | 55.01 |  | 0.35 |  | 1 |  | 1
838mm x 0.15 DDP SL | 0 | 0 |  | 0.675 | 0.4 | 0.5 | 0.5 | 1 | 1
838mm x 0.25 DDP SL | 57.51 | 1 |  | 0.675 | 0.45 | 1 |  | 3
[5 empty] | 0.5 |  | 1 |  | 2
HV strip insulations thickness |  |  | 55.01 |  | 0.55 | 0.67 | 0.33 | 2 | 1
45 x 0.05 mm Strip | 0 | 0 |  |  | 0.6 | 1 |  | 4
45 x 0.075 mm Strip | 0 | 0 |  |  | 0.65 |  | 1 |  | 2
[5 empty] | 0.7 | 0.75 | 0.25 | 3 | 1
838mm x 0.15 DDP DL | 0 |  |  |  | 0.75 |  | 1 |  | 3
838mm x 0.15 DDP SL | 0 |  |  |  | 0.8 | 0.5 | 0.5 | 2 | 2
838mm x 0.25 DDP SL | 72.71 |  |  |  | 0.85 | 0.8 | 0.2 | 4 | 1 | Edge Strips
[5 empty] | 0.9 | 0.25 | 0.75 | 1 | 3 | 8
LV edge strip | 18 |  |  |  | 0.95 |  | 1 |  | 3 | 18
40 | 0.8 | 13 | 19 |  | 1.00 |  | 1 |  | 4 | 27
918.961 | 16.0 | 3 | 10 | 3 | 1.1 | 0.66667 | 0.33333 | 4 | 2 | 33
| #VALUE! |  |  |  | 1.2 | 1 |  | 8 | 0 | 45
14703.376 | 1.2139 |  |  |  | 1.25 |  | 1 | 0 | 4
18 | 0.25 |  |  |  | 1.3 | 0.67 | 0.33 | 4 | 2
HV edge strip | 45 |  |  |  | 1.4 | 0.75 | 0.25 | 6 | 2
90 | 3.000 | 12 | 18 |  | 1.5 |  | 1 |  | 6
1437.4 | 20 |  |  |  | 1.6 | 0.5 | 0.5 | 4 | 4
28748 | 20.0259 |  |  |  | 1.7 | 0.8 | 0.2 | 8 | 2
45 | 0.25 |  |  |  | 1.8 | 0.25 | 0.75 | 2 | 6
Duct Space |  |  |  |  | 1.9 |  | 1 |  | 6
LV | 1.36 | 19 | 13 | 6 | 2 |  | 1 |  | 8
HV | 2.12 | 19 | 13 | 6 | 2.1 | 0.4 | 0.6 |  | 8
| 3.48 |  |  |  | 2.2 | 0.66667 | 0.33333 | 1 | 8
Corragated Board |  |  |  |  | 2.3 | 0.17 | 0.83 | 2 | 10
| 35.54 | 7 |  |  | 2.45 | 0.23 | 0.77 | 3 | 10
CORE STEEL
Core Steel | Builds(mm) | Weight(kg) | : | . | "(10)" | "m" | *100 | "k" | Weight | Adjusted Build
190 | 92 | 673.1 | 7 | 13 | 92 | 8 | 0 | 19 | 673.1 | #VALUE! |  | 190
180 | 62 | 426.3 | 7 | 13 | 62 | 8 | 0 | 19 | 426.3 | 62 |  | 180 | #VALUE! | #VALUE!
160 | 42 | 255.5 | 7 | 13 | 42 | 8 | 0 | 19 | 255.5 | 42 |  | 160 | #VALUE!
140 | 26 | 140.3 | 7 | 13 | 26 | 8 | 0 | 19 | 140.3 | 26 |  | 140 | #VALUE!
120 | 19 | 87.3 | 7 | 13 | 19 | 8 | 0 | 19 | 87.3 | #VALUE! |  | 120
0 | 0 | 0 | 7 | 13 | 0 | 7 | 0 | 18 | 0.0 | 0 |  |  | 120
0 | 0 | 0 | 7 | 13 | 0 | 7 | 0 | 18 | 0.0 | 0
0 | 0 | 0 | 7 | 13 | 0 | 7 | 0 | 18 | 0.0 | 0
0 | 0 | 0 | 7 | 13 | 0 | 7 | 0 | 18 | 0.0 | 0
TOTAL | 241 | 1582.4 | 1582.4
core steel type | 23ZDKH
core steel thickness | 23ZDKH85
COPPER
LV | CU-foil
AL-foil
CU-layer-rect
HV | CU-round
CU-rectangular
LV Cu
AL-Foil | 800.00 x 0.80 | 19 | 4 | 2
AL-Foil | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| 800.00 x 0.80 | 800 | 0.8
800.00 x 0.80mm AL-Foil | 152.44 | 152.44
HV Cu
AL-Round | 3.000 x 3.000 | 18 | 12 | 4 | 2 | 2
3.000
3.000 x 3.000mm AL-Round | 380.88 | 380.88
Flat Cu
LV Leads | 17.07 | 8 | 17
Bus Bars | 8
Total | 25.07 |  | 10 | 100 | 18 | 9 | 19
10*100mm | 2.8169
Inhibited Mineral Oil | 1381.6092
STEEL
Steel Density (kg/mm3) | 7.85e-06
Steel Weights | From Program | Calculated
Cover | 74 | 114.3557 | 3 | 11
Case + Cooling | 471
Case | 85 | 141.7224
Clamps | 219 | 67.9075 | 5
Conservator | 0 | 0 | #VALUE!
| 378 | 324
378
Radiator Weights
Fin Type Radiators | 386 | 15 | 10
Panel Type Radiators | 0 | 6
386
386
Galvanize | 545
Steel Channel
MS Ch 76x38x6 , L= 1614mm | 840
MS Ch 100x50x6 , L= 1614mm | 1128
MS Ch 127x64x6 , L= 1614mm | 1458
MS Ch 152x76x6 , L= 1614mm | 1752
MS Ch 200x75x9 , L= 1614mm | 2988
4mm MS Plate 1614x280.5x4mm | 1122
Base Skid
50x50x6 AI | 50 | 564
76x38x6 MS Channel | 76 | 840 |  | 400 upto including
100x50x6 MS Channel | 100 | 1128 |  | 1000 upto inc
152x152x10 H Iron | 152 | 4360 |  | 2500
250x75x9 MS Channel | 200 | 2988 |  | >2500
| Dimensions |  |  | MS Plate Arrangement-I |  |  | MS Plate Arrangement-II |  |  |  |  | WEIGHT
MS Sheet -Length | 2440
MS Sheet -Width | 1220
| Thickness | Width | Length | L/L | W/W | Nos | L/W | W/L | Nos | Nos of transformer | Required Nos
Cover plate | 10 | 790 | 1844 | 1 | 1 | 1 | 3 | 0 | 0 | 1 | 15 | 114.3557
Base | 6 | 1784 | 1084 | 2 | 0 | 0 | 1 | 1 | 1 | 1 | 15 | 91.0846
Conservator | 3 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 0
Nos of Sheets
Tank | 6 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
| Thickness | Width | Length | Description | Qty | CSA | WEIGHT
Stay rod | 12 | - | 1325 | 12mm BS Rod | 0 | 114
Tie Rod | 12 | - | 369 | 12mm BS Rod | 4 | 114
Flange Long side | 6 | 80 | 1784 | 80x80x6 Angle Iron | 2 | 924 | 25.8801
Flange Short side | 6 | 80 | 730 | 80x80x6 Angle Iron | 2 | 924 | 10.59 |  |  |  | cons
Traverse-Horizontal | 10 | 75 | 241 | 75x10 Flat Iron | 0 | 750 | 0
Traverse-Vertical | 10 | 75 | 270 | 75x10 Flat Iron | 0 | 750 | 0
Foot | 20 | 75 | 469 | 75x20 Flat Iron | 2 | 1500 | 11.0449
Base Skid | - | 100 | 800 | 100x50x6 MS Channel | 2 | 1128 | 14.1677
Steel Channel | 4 | 280.5 | 1614 | 4 mm MS Plate | 4 | 1122 | 56.8625
Wooden cross cut height | 10 | 71 | 1250 | 0 | 0 | 710
Wooden clamp height | 160 | 40 | 1604 | 0 | 0 | 6400
COOLING
Panel Radiators | NO | 16
1300/1300/1300/1300 | 0 | 0 | 0
No of radiators | 0
Elements/radiator | 0
Center to center distance | 0
Depth of a radiator | 90
Width of radiator flange | 150
Radiator width | 520
Distance bet 2 radiators | 80
Offset for off-central type | 131
PANEL TYPE RADS | LV | HV | Cons. Side | Other Side | Length Addition | Width Addition
1 | 1 | 0 | 0 | 0 | 0 | 90
1 | 2 | 0 | 0 | 0 | 0 | 90
3 | 2 | 1 | 0 | 0 | 0 | 180
4 | 2 | 2 | 0 | 0 | 0 | 180
5 | 2 | 2 | 1 | 0 | 90 | 180
6 | 2 | 2 | 2 | 0 | 90 | 180
7 | 2 | 2 | 2 | 1 | 180 | 180
8 | 2 | 2 | 2 | 2 | 180 | 180
Fin depth-long side | 260 | 9 | 4
Fin depth-short side | 100
Fin height | 1300 | 5
Fin Thickness | 1300 | 1.5 | 1.5 | 10 | 5
Labour Hours |  |  | 0 | #REF!
| 10 |  |  | 0
| 10 |  |  | 0
#REF!
ACCESSORIES
HV Bushings | Plug-in Type 36 kV 250 A Interface B |  |  | 150 | 3 | 5 | 3
170 | 36 | 170 | 250 |  |  |  | 4
Selection | Voltage (kV) | BIL (kV) | Current (A) | Height (mm) | Description | Weight (kg)
0 | 12 | 75 | 250 | 310 | 10 NF 250 CD = 372 mm P-4 EN | 5.65
0 | 12 | 75 | 630 | 342 | 10 NF 630 | 8
0 | 12 | 75 | 250 | 150 | 1M (B9722) | 5
0 | 24 | 125 | 250 | 310 | 24 NF 250 P3 CD = 605 mm | 5.65
0 | 24 | 125 | 250 | 150 | Plug-in Type 24 kV 250 A Interface B | 5
0 | 24 | 125 | 630 | 150 | Plug-in Type 24 kV 630 A Interface C | 6.5
0 | 36 | 200 | 250 | 520 | 30 NF 250 CD = 900 mm P-3 EN | 9.35
0 | 36 | 200 | 250 | 520 | 30 NF 250 CD = 1116 mm | 12.55
0 | 36 | 200 | 250 | 520 | 30 NF 250 CD = 1920 mm | 12.55
1 | 36 | 170 | 250 | 150 | Plug-in Type 36 kV 250 A Interface B | 5
0 | 36 | 170 | 630 | 150 | Plug-in Type 36 kV 630 A Interface C | 6.5
0 | 52 | 250 | 1000 | 150 | Plug-in Type 52 kV 1000 A Interface F | 8
0 | 42 | 200 | 250 | 500 | 40 NF 250 | 15
0 | 52 | 250 | 1000 | 730 | 52 NF 1000 CD = 1430 mm | 35.2
LV Bushings | EN 2000 |  | 240 | 6.24 | 4 |  | 3
1391.205 | 1 | 2000 |  |  |  |  | 4
Selection | Voltage (kV) | Current (A) | Height (mm) | Weight (kg) | Description |  | 6
8
0 | 1 | 250 | 120 | 0.43 | EN 250 | 250
0 | 1 | 630 | 165 | 1.16 | EN 630 | 630
0 | 1 | 1250 | 177 | 2.73 | EN 1250 | 1250
1 | 1 | 2000 | 240 | 6.24 | EN 2000 | 2000
0 | 1 | 2500 | 177 | 2.73 | EN 1250 | 1250
0 | 1 | 3150 | 250 | 8.45 | EN 3150 | 3150
0 | 1 | 4000 | 240 | 6.24 | EN 2000 | 2000
0 | 1 | 6300 | 250 | 8.45 | EN 3150 | 3150
0 | 12 | 250 | 310 | 5.65 | 10 NF 250 | 250
0 | 12 | 630 | 310 | 8 | 10 NF 630 | 630
0 | 12 | 250 | 150 | 5 | 1M (B9722) | 250
0 | 24 | 250 | 150 | 5 | Plug-in Type 24 kV 250 A Interface B | 250
0 | 24 | 630 | 150 | 6.5 | Plug-in Type 24 kV 630 A Interface C | 630
Tap selector | HM 23.44.885 (30kV 30A 131mm 5 Pos) | [5 empty] | 0
1 | 30 | 30 | 200 | 5 |  |  | 1
Selection | Voltage (kV) | Current (A) | BIL (kV) | Positions | Description
0 | 20 | 30 | 95 | 5 | HR 7A3.235 (20kV 30A 100mm 5 Pos)
0 | 20 | 30 | 95 | 7 | HR 7A3.235 (20kV 30A 100mm 7 Pos)
0 | 20 | 63 | 95 | 5 | HM 25.43.885 (20kV 63A 131mm 5 Pos)
0 | 20 | 120 | 95 | 5 | HM 28.43.885 (20kV 120A 131mm 5 Pos)
0 | 20 | 250 | 95 | 5 | HM 28.43.885 (20kV 250A 131mm 5 Pos)
0 | 30 | 30 | 200 | 5 | HR 7A3.335 (30kV 30A 100mm 5 Pos)
0 | 30 | 30 | 200 | 7 | HR 7A3.335 (30kV 30A 100mm 7 Pos)
1 | 30 | 30 | 200 | 5 | HM 23.44.885 (30kV 30A 131mm 5 Pos)
0 | 30 | 30 | 200 | 7 | HM 23.44.885 (30kV 30A 131mm 7 Pos)
0 | 30 | 63 | 200 | 5 | HM 25.44.885 (30kV 63A 131mm 5 Pos)
Valves
PRV T-10K1 1R"
PRV T-50 0.4 BAR
DRAIN VALVE NW 31
AIR RELEASE PLUG
ARES DIN25 DOUBLE FLANGE GATE VALVE
SINGLE FLANGE BALL VALVE 1" NW25S-SS
THROTTLE VALVE FOR RADIATOR NW80 FORMB
BALL VALVE 1" PELGER
GATE VALVE WITH SAMPLING
GATE VALVE WITHOUT SAMPLING
SAMPLING VALVE
BALL VALVE 1" Threaded on both sides
Oil Level Indicators
Magnetic- with 400mm boss
Magnetic- with 200mm boss
4 HOLES PRISMATIC
6 HOLES PRISMATIC
8 HOLES PRISMATIC
FLOATING TYPE
VIAT SO4 - Dial Type with Contacts
VIAT SO6 - Dial Type with Contacts
Cable Boxes | [5 empty] | HV Cable Boxes | Selection | Price | Depth | Width | H above cover | Weight
HV CABLE BOX | 350 |  |  |  |  | Plug-In Cable Box | 1 | 350 | 1052 | 747 | 391 | 100
LV CABLE BOX | 800 |  |  |  |  | 1M Cable Box | 0 | 350 | 862 | 578 | 318 | 57
WTI BOX | 0
CONNECTOR BOX | 0 |  |  |  |  | LV Cable Boxes |  | Price | Depth | Width | H above cover | Weight
HV ENCLOSURE | 0 |  |  |  |  | EN 250 | 0 | 500 | 933 | 770 | 331 | 85
Other Parts | [5 empty] | EN 630 | 0 | 600 | 933 | 770 | 331 | 135
RATING PLATE | [5 empty] | EN 1250 | 0 | 700 | 1085 | 1073 | 386 | 150
PHASE MARKING PLATES | [5 empty] | EN 1250 x 2 | 0 | 750 | 1085 | 1073 | 386 | 180
S/A MOUNTING BRACKET | [5 empty] | EN 2000 | 1 | 800 | 1065 | 1115 | 431 | 200
ISD UNIT | [5 empty] | EN 2000 x 2 | 0 | 850 | 1420 | 1115 | 431 | 230
BREATHER 1KG TYPE A | [5 empty] | EN 3150 | 0 | 900 | 1140 | 1185 | 518 | 300
BREATHER 1KG TYPE B | [5 empty] | EN 3150 x 2 | 0 | 950 | 1495 | 1133 | 518 | 340
BREATHER 1KG TYPE C
BREATHER 2KG | [5 empty] | WTI Box | 0 | 250 | 400 | 700 | 500 | 10
THERMOMETER TEK 16 | [5 empty] | Connector Box | 0 | 150 | 300 | 500 | 300 | 5
THERMOWELL 3/4" BSP | [5 empty] | HV Enclosure | 0 | 250 | 630 | 750 | 400 | 15
THERMOMETER POCKET
GALVANIZED CUP FOR THERMOMETER POCKET
BUCHOLZ RELAY EW712
CONSERVATOR FILLING CAP AL. 2"
T/F WHEEL 7613T00691 |  |  |  | SDF |  | HRC Fuse
T/F WHEEL 7613T00691 |  |  |  | Current | 0 | 0
WINDING TEMP. INDICATOR TD50 (354 01 12X6.0) |  |  |  | 20 | 20A 3KL81113HA10
WINDING TEMP. INDICATOR TD76 (354 01 12X6.0) |  |  |  | 32 | 32A 3KL81213HA10
RTD WTI (PT100) |  |  |  | 63 | 63A 3KL81513HA10
RTD OTI (PT100) |  |  |  | 100 | 100A 3KL82113HA10
CT 3000/2A Oil Immersed (Measuring) Ring Type 15VA/0.5 |  |  |  | 125 | 125A 3KL82213HA10
CT 5000/5A Oil Immersed (Measuring) Ring Type 15VA/0.5 |  |  |  | 160 | 160A 3KL82313HA10
CT 1600/1A 5P20 15VA/0.5 2 Core |  |  |  | 200 | 200A 3KL83113HA10
NCT 400/1A 5P20 15VA |  |  |  | 250 | 250A 3KL83213HA10
NCT 1600/1A 5P20 15VA |  |  |  | 315 | 315A 3KL83313HA10
NCT 2000/1A 5P20 15VA |  |  |  | 400 | 400A 3KL83413HA10
CT TERMINAL BOX (2 TERMINALS) |  |  |  | 500 | 500A 3KL84113HA10
CT TERMINAL BOX (4 TERMINALS) |  |  |  | 630 | 630A 3KL84213HA10
CT TERMINAL BOX (6 TERMINALS) |  |  |  | 800 | 800A 3KL84313HA10
24kV ELBOW CONNECTOR SET (03)
36kV ELBOW CONNECTOR SET (03)
52kV ELBOW CONNECTOR SET (04)
OBO SURGE ARRESTERS
LTL Name Board
Nut, Bolt & 2 Washers (Galvanized) M10 x 40 mm
Split washers for tank cover fixing
M12 bolt, nut, spring washer & lock washer for earthing terminal
Flange Gasket
Wooden Pallete For Packing
Painting |  |  |  |  | Capacity | 2 Coat Sys - DFT 130 |  | 3 Coat Sys - DFT 250
GALVANIZING |  |  | 0 |  | 1250 | Primer (kg) | Powder (kg) | Primer (kg) | Powder (kg)
PRIMER PAINT & THINNER |  |  | 15 |  | 250 | 5 | 6 | 10 | 6
POWDER PAINT (RAL6028) |  |  | 20 |  | 800 | 10 | 15 | 20 | 15 |  | 30
INTERNAL PAINT |  |  | 15 |  | 1250 | 15 | 20 | 30 | 20
[5 empty] | 2000 | 20 | 30 | 40 | 30
Cooling Ducts |  |  |  |  | 2500 | 25 | 30 | 50 | 30
LV No. of Cooling Ducts | 1 |  |  |  | 3150 | 30 | 40 | 60 | 40
LV MTL | 918.961 |  |  |  | 4000 | 40 | 50 | 70 | 50
LV No. of Layers | 16 |  |  |  | 5000 | 50 | 60 | 80 | 60
LV Cooling duct height | 838
| 0.33 | 8 |  |  | 1/3 Cooling Duct Between Layers 8 & 9 (838 x 310 mm)
| 0.67 | 8 |  |  | 2/3 Cooling Duct Between Layers 8 & 9 (838 x 610 mm)
| 1 | 8 |  |  | Full Cooling Duct Between Layers 8 & 9 (838 x 920 mm)
| 1.33 | 6 | 11 |  | Full Cooling Duct Between Layers 6 & 7 (838 x 830 mm) | 1/3 Cooling Duct Between Layers 11 & 12 (838 x 340 mm)
| 1.67 | 6 | 11 |  | Full Cooling Duct Between Layers 6 & 7 (838 x 830 mm) | 2/3 Cooling Duct Between Layers 11 & 12 (838 x 670 mm)
| 2 | 5 | 10 |  | Full Cooling Duct Between Layers 5 & 6 (838 x 830 mm) | Full Cooling Duct Between Layers 10 & 11 (838 x 1010 mm)
| 2.33 | 4 | 9 | 12 | Full Cooling Duct Between Layers 4 & 5 (838 x 780 mm) | Full Cooling Duct Between Layers 9 & 10 (838 x 920 mm) | 1/3 Cooling Duct Between Layers 12 & 13 (838 x 350 mm)
| 2.67 | 4 | 8 | 12 | Full Cooling Duct Between Layers 4 & 5 (838 x 780 mm) | Full Cooling Duct Between Layers 8 & 9 (838 x 920 mm) | 2/3 Cooling Duct Between Layers 12 & 13 (838 x 700 mm)
| 3 | 4 | 8 | 12 | Full Cooling Duct Between Layers 4 & 5 (838 x 780 mm) | Full Cooling Duct Between Layers 8 & 9 (838 x 920 mm) | Full Cooling Duct Between Layers 12 & 13 (838 x 1060 mm)
HV No. of Cooling Ducts | 1
HV MTL | 1437.4
HV No. of Layers | 20
HV Cooling duct height | 838
| 0.33 | 10 |  |  | 1/3 Cooling Duct Between Layers 10 & 11 (838 x 480 mm)
| 0.67 | 10 |  |  | 2/3 Cooling Duct Between Layers 10 & 11 (838 x 960 mm)
| 1 | 10 |  |  | Full Cooling Duct Between Layers 10 & 11 (838 x 1440 mm)
| 1.33 | 8 | 14 |  | Full Cooling Duct Between Layers 8 & 9 (838 x 1290 mm) | 1/3 Cooling Duct Between Layers 14 & 15 (838 x 530 mm)
| 1.67 | 7 | 13 |  | Full Cooling Duct Between Layers 7 & 8 (838 x 1290 mm) | 2/3 Cooling Duct Between Layers 13 & 14 (838 x 1050 mm)
| 2 | 6 | 13 |  | Full Cooling Duct Between Layers 6 & 7 (838 x 1290 mm) | Full Cooling Duct Between Layers 13 & 14 (838 x 1580 mm)
| 2.33 | 6 | 12 | 16 | Full Cooling Duct Between Layers 6 & 7 (838 x 1220 mm) | Full Cooling Duct Between Layers 12 & 13 (838 x 1440 mm) | 1/3 Cooling Duct Between Layers 16 & 17 (838 x 550 mm)
| 2.67 | 5 | 10 | 15 | Full Cooling Duct Between Layers 6 & 6 (838 x 1220 mm) | Full Cooling Duct Between Layers 10 & 11 (838 x 1440 mm) | 2/3 Cooling Duct Between Layers 15 & 16 (838 x 1100 mm)
| 3 | 5 | 10 | 15 | Full Cooling Duct Between Layers 5 & 6 (838 x 1220 mm) | Full Cooling Duct Between Layers 10 & 11 (838 x 1440 mm) | Full Cooling Duct Between Layers 15 & 16 (838 x 1650 mm)
Note on D81: Eranga: VALUE(LEFT(P!C82,FIND(".",P!C82,1)-1))
Note on D82: Eranga: VALUE(LEFT(P!C83,FIND(".",P!C83,1)-1))
Note on B83: Eranga: =ROUNDUP(C79*100,2)
Note on B84: Eranga: =MROUND(D80*C80+2,5)
Note on B85: Eranga: =MROUND(D81*C81/B84+2,5)
Note on C140: Eranga Anuradha Bala: =IF(AND(B47<30000,B46<=400),B134-2,IF(VALUE(B134)<611,B134,MROUND(B134-3,5)))
Note on G153: Eranga: Double foil 0.15 DL x 2
Note on G211: Eranga: Axial Parallel

## Bill of Materials
Bill of Materials
Transformer Type: |  | 1000kVA 33000/415V
Contract No.: |  | TD EDCO
Customer: |  | EDCO
No of Transformers: |  | 15
| Material | Description | Unit | Qty | Unit Price | Cost | % | Total Quantity | Per Winding Quantity
| MAJOR MATERIALS |  |  | xxx
1 | Oil | Inhibited Mineral Oil | L | 1381.6092 | 0.98 | 1353.977 | 8.243% | 20724.1379
2
LV Winding
3 | LV Conductor | 800.00 x 0.80mm AL-Foil | kg | 152.44 | 3.89 | 592.9916 | 3.61% | 2286.6 | 50.8133
4 | Cuopanal Bus Bar | 10*100mm | kg | 25.07 | 3.89 | 97.5223 | 0.5938% | 376.05 | 8.3567
5 | DDP Double Layer | 838mm x 0.15 DDP DL | kg | 0 | 7.6966 | 0 | 0% | 0 | 0
6 | DDP Single Layer | 838mm x 0.15 DDP SL | kg | 0 | 4.5069 | 0 | 0% | 0 | 0
7 | DDP Single Layer | 838mm x 0.25 DDP SL | kg | 15.2 | 4.5069 | 68.5053 | 0.4171% | 228 | 5.0667
8 | LV Edge Strip | 18 x 0.25mm | kg | 1.2139 | 4.9321 | 5.9871 | 0.03645% | 18.2087 | 0.40464
9 | LV Insulation Packet | 1000/33 TD EDCO INLV | Nos. | 3 | 10 | 30 | 0.1827% | 45
10 | [6 empty] | 0% | 0
HV Winding
11 | HV Conductor | 3.000 x 3.000mm AL-Round | kg | 380.88 | 4.85 | 1847.268 | 11.25% | 5713.2 | 126.96
12 | DDP Single Layer | 838mm x 0.15 DDP SL | kg | 0 | 4.5069 | 0 | 0% | 0 | 0
13 | DDP Single Layer | 838mm x 0.25 DDP SL | kg | 57.51 | 4.63 | 266.2713 | 1.621% | 862.65 | 19.17
14 | HV Strip Insulation | 45 x 0.075 mm Strip | kg | 0 | 3.4698 | 0 | 0% | 0 | 0
15 | HV Edge Strip | 45 x 0.25mm | kg | 20.0259 | 4.9321 | 98.7696 | 0.6013% | 300.3879 | 6.6753
16 | HV Insulation Packet | 1000/33 TD EDCO INHV | Nos. | 3 | 90 | 270 | 1.644% | 45
17
Assembly
18 | HD Copper | 3 mm | kg | 8 | 12.8622 | 102.8976 | 0.6265% | 120
19 | Bare Copper | 7/1.7 mm | kg | 0 | 12.8622 | 0 | 0% | 0
20 | Bare Copper | 19/1.35 mm | kg | 0 | 12.8622 | 0 | 0% | 0
21 | Copper Flexible | 1000/33 TD EDCO CUFX | Nos. | 4 | 75 | 300 | 1.827% | 60
22 | Timber Packet | 1000/33 TD EDCO TMBC & TMAS | Nos. | 1 | 65 | 65 | 0.3957% | 15
23 | Insulation Packet | 1000/33 TD EDCO INBC & INAS | Nos. | 1 | 90 | 90 | 0.548% | 15
24 | Shark Connectors |  | Nos. |  | 3.5 | 0 | 0% | 0
24 | [5 empty] | 0 | 0% | 0
| CORE STEEL |  | kg | 1582.4 | 3.88 | 6139.712 | 37.38% | 23736
21 | 23ZDKH85 | 190mm | kg | 673.1 |  | 0 | 0% | 10096.5
22 | 23ZDKH85 | 180mm | kg | 426.3 | 0 | 0 | 0% | 6394.5 |  | General Choice
23 | 23ZDKH85 | 160mm | kg | 255.5 | 0 | 0 | 0% | 3832.5 |  | 1250/33/400 EU AL Tank | 1000/33/415 EU AL | AL
24 | 23ZDKH85 | 140mm | kg | 140.3 | 0 | 0 | 0% | 2104.5
25 | 23ZDKH85 | 120mm | kg | 87.3 | 0 | 0 | 0% | 1309.5 |  | Custom Choice
26 | 0 | 0 | kg | 0 | 0 | 0 | 0% | 0
27 | 0 | 0 | kg | 0 | 0 | 0 | 0% | 0
28 | 0 | 0 | kg | 0 | 0 | 0 | 0% | 0
29 | 0 | 0 | kg | 0 | 0 | 0 | 0% | 0
| STEEL |  |  | xxx | [5 empty] | Special Requirements
30 | Trava, Foot & Clamps |  | kg | 219 | 2 | 438 | 2.667% | 3285 |  | Cover Plate Thickness
31 | Fin Type Radiators | 1250/33/400 EU AL Tank | kg | 565 | 3.35 | 1892.75 | 11.52% | 8475 |  | Base Thickness
32 | Pole Mounting Bracket |  | Nos. |  | 15 | 0 | 0% | 0
33 | [9 empty] | Tank Wall Thickness
| ACCESSORIES |  |  | xxx
HV Bushings
33 | Plug-in Type 36 kV 250 A Interface B |  | Nos. | 3 | 48.74 | 146.22 | 0.8902% | 45 |  | Plug-in Type 36 kV 250 A Interface B
34 | HV Cable Lugs |  | Nos. |  | 2.55 | 0 | 0% | 0
| LV Bushings |  |  |  |  | 0 | 0%
35 | EN 2000 |  | Nos. | 4 | 120.65 | 482.6 | 2.938% | 60 |  | EN 2000
36 | LV Cable Lugs |  | Nos. |  | 2.88 | 0 | 0% | 0
| Tap selector |  |  |  |  | 0 | 0%
37 | HR 7A3.335 (30kV 30A 100mm 5 Pos) |  | Nos. | 1 | 24.97 | 24.97 | 0.152% | 15 |  | HR 7A3.335 (30kV 30A 100mm 5 Pos)
38
| Valves |  |  |  |  | 0 | 0%
39 | PRV T-10K1 1R" |  | Nos. | 1 | 7.76 | 7.76 | 0.04725% | 15
40 | PRV T-50 0.4 BAR |  | Nos. |  | 107.5224 | 0 | 0% | 0
41 | DRAIN VALVE NW 31 |  | Nos. | 1 | 11.46 | 11.46 | 0.06977% | 15
42 | AIR RELEASE PLUG |  | Nos. |  |  | 0 | 0% | 0
43 | ARES DIN25 DOUBLE FLANGE GATE VALVE |  | Nos. |  | 93.525 | 0 | 0% | 0
44 | SINGLE FLANGE BALL VALVE 1" NW25S-SS |  | Nos. |  |  | 0 | 0% | 0
45 | THROTTLE VALVE FOR RADIATOR NW80 FORMB |  | Nos. | 0 |  | 0 | 0% | 0
46 | BALL VALVE 1" PELGER |  | Nos. | 0 | 10.5724 | 0 | 0% | 0
47 | GATE VALVE WITH SAMPLING |  | Nos. |  | 63.423 | 0 | 0% | 0
48 | GATE VALVE WITHOUT SAMPLING |  | Nos. | 0 |  | 0 | 0% | 0
49 | SAMPLING VALVE |  | Nos. |  |  | 0 | 0% | 0
50 | BALL VALVE 1" Threaded on both sides |  | Nos. |  |  | 0 | 0% | 0
51 | [5 empty] | 0 | 0% | 0
| Oil Level Indicators |  |  |  |  | 0 | 0%
52 | Magnetic- with 400mm boss |  | Nos. | 0 |  | 0 | 0% | 0
53 | Magnetic- with 200mm boss |  | Nos. |  | 23.1319 | 0 | 0% | 0
54 | 4 HOLES PRISMATIC |  | Nos. | 1 | 10.2201 | 10.2201 | 0.06222% | 15
55 | 6 HOLES PRISMATIC |  | Nos. |  | 14.89 | 0 | 0% | 0
56 | 8 HOLES PRISMATIC |  | Nos. |  | 15.2671 | 0 | 0% | 0
57 | FLOATING TYPE |  | Nos. |  | 6.3087 | 0 | 0% | 0
58 | VIAT SO4 - Dial Type with Contacts |  | Nos. |  | 104.0936 | 0 | 0%
59 | VIAT SO6 - Dial Type with Contacts |  | Nos. |  | 157.7176 | 0 | 0%
60 | [5 empty] | 0 | 0%
| Cable Boxes |  |  |  |  | 0 | 0%
61 | HV CABLE BOX |  | Nos. | 1 | 600 | 600 | 3.653% | 15
62 | LV CABLE BOX |  | Nos. | 1 | 600 | 600 | 3.653% | 15
63 | WTI BOX |  | Nos. |  | 0 | 0 | 0% | 0
64 | CONNECTOR BOX |  | Nos. |  | 150 | 0 | 0% | 0
65 | HV ENCLOSURE |  | Nos. |  | 0 | 0 | 0% | 0
66
| Other Parts |  |  |  |  | 0 | 0%
67 | RATING PLATE |  | Nos. | 1 | 4.5685 | 4.5685 | 0.02781% | 15
68 | PHASE MARKING PLATES |  | Nos. | 1 | 2.335 | 2.335 | 0.01422% | 15
69 | S/A MOUNTING BRACKET |  | Nos. | 0 | 14.467 | 0 | 0% | 0
70 | ISD UNIT |  | Nos. |  | 246.0394 | 0 | 0% | 0
71 | BREATHER 1KG TYPE A |  | Nos. | 0 | 20.7 | 0 | 0% | 0
72 | BREATHER 1KG TYPE B |  | Nos. | 0 | 26.0156 | 0 | 0% | 0
73 | BREATHER 1KG TYPE C |  | Nos. |  | 22.2991 | 0 | 0% | 0
74 | BREATHER 2KG |  | Nos. | 0 |  | 0 | 0% | 0
75 | THERMOMETER TWO CONTACTS |  | Nos. | 1 | 80.38 | 80.38 | 0.4894% | 15
76 | THERMOWELL 3/4" BSP |  | Nos. | 1 | 10 | 10 | 0.06088% | 15
77 | THERMOMETER POCKET |  | Nos. | 1 | 2.5 | 2.5 | 0.01522% | 15
78 | GALVANIZED CUP FOR THERMOMETER POCKET |  | Nos. |  | 2.5 | 0 | 0% | 0
79 | BUCHOLZ RELAY EW712 |  | Nos. | 0 | 257.6053 | 0 | 0% | 0
80 | CONSERVATOR FILLING CAP AL. 2" |  | Nos. | 0 | 10.1523 | 0 | 0% | 0
81 | T/F WHEEL 7613T00691 |  | Nos. |  | 16.3527 | 0 | 0% | 0
82 | T/F WHEEL 7613T00691 |  | Nos. |  |  | 0 | 0% | 0
83 | WINDING TEMP. INDICATOR TD50 (354 01 12X6.0) |  | Nos. |  |  | 0 | 0% | 0
84 | WINDING TEMP. INDICATOR TD76 (354 01 12X6.0) |  | Nos. |  |  | 0 | 0% | 0
85 | RTD WTI (PT100) |  | Sets. |  |  | 0 | 0% | 0
86 | RTD OTI (PT100) |  | Sets. |  |  | 0 | 0% | 0
87 | CT 3000/2A Oil Immersed (Measuring) Ring Type 15VA/0.5 |  | Nos. |  | 50 | 0 | 0% | 0
88 | CT 5000/5A Oil Immersed (Measuring) Ring Type 15VA/0.5 |  | Nos. |  | 60 | 0 | 0% | 0
89 | CT 1600/1A 5P20 15VA/0.5 2 Core |  | Nos. |  | 170.1 | 0 | 0% | 0
90 | NCT 400/1A 5P20 15VA |  | Nos. |  | 400 | 0 | 0% | 0
91 | NCT 1600/1A 5P20 15VA |  | Nos. |  | 127.575 | 0 | 0% | 0
92 | NCT 2000/1A 5P20 15VA |  | Nos. |  | 297.675 | 0 | 0% | 0
93 | CT TERMINAL BOX (2 TERMINALS) |  | Nos. |  |  | 0 | 0% | 0
94 | CT TERMINAL BOX (4 TERMINALS) |  | Nos. |  | 77.3035 | 0 | 0% | 0
95 | CT TERMINAL BOX (6 TERMINALS) |  | Nos. |  |  | 0 | 0% | 0
96 | 24kV ELBOW CONNECTOR SET (03) |  | Nos. | 0 |  | 0 | 0% | 0
97 | 36kV ELBOW CONNECTOR SET (03) |  | Nos. | 0 |  | 0 | 0% | 0
98 | 52kV ELBOW CONNECTOR SET (04) |  | Nos. | 0 |  | 0 | 0% | 0
99 | OBO SURGE ARRESTERS |  | Nos. | 0 |  | 0 | 0% | 0
100 | LTL Name Board |  | Nos. |  | 7.027 | 0 | 0% | 0
101 | Nut, Bolt & 2 Washers (Galvanized) M10 x 40 mm |  | Nos. |  |  | 0 | 0% | 0
102 | Split washers for tank cover fixing |  | Nos. |  |  | 0 | 0% | 0
103 | M12 bolt, nut, spring washer & lock washer for earthing terminal |  | Nos. |  | 178.64 | 0 | 0% | 0
104 | Flange Gasket |  | Nos. |  | 600 | 0 | 0% | 0
105 | Wooden Pallete For Packing |  | Nos. |  | 60 | 0 | 0% | 0
105 | EN 250 for core earthing |  | Nos. |  | 14.19 | 0 | 0% | 0
| Painting |  |  |  |  | 0 | 0%
106 | GALVANIZING |  | kg | 0 | 0.30843 | 0 | 0% | 0
107 | PRIMER PAINT & THINNER |  | kg |  | 9.2 | 0 | 0% | 0
108 | POWDER PAINT (RAL6028) |  | kg |  | 5.26 | 0 | 0% | 0
109 | INTERNAL PAINT |  | kg |  | 7.6837 | 0 | 0% | 0
| 0 |  |  | 0 |  | 0 | 0% | 0
| Major Material |  | $ | * * * |  | 13659.6519 | 83.16% | 204894.7778
| Accessories |  | $ | * * * |  | 1983.0137 | 12.07% | 29745.2048
| Miscellaneous |  | $ | * * * | 5% | 782.1333 | 4.762% | 11731.9991
| Total Materials |  | $ | * * * |  | 16424.7988 | #DIV/0! | 246371.9816
Design Engineer
-
Note on L45: Eranga: If different radiator is used, type it here.

## Radiator Choise
Standard Copper EU2021 Radiators | 1000/33/415 EU | 1000/33/415 EU Tank
| 1000/33/400 EU | 1250/33/415 EU Tank
| 1000/33/440 EU | 1250/33/415 EU Tank
| 1000/33/690 EU | 1250/33/415 EU Tank
| 1000/33/800 EU | 1250/33/415 EU Tank
| 1250/33/415 EU | 1250/33/415 EU Tank
| 1250/33/400 EU | 1250/33/400 EU Tank
| 1250/33/440 EU | 1250/33/400 EU Tank
| 1250/33/690 EU | 1250/33/400 EU Tank
| 1250/33/800 EU | 1250/33/400 EU Tank
| 1600/33/415 EU | 1600/33/400 EU Tank
| 1600/33/400 EU | 1600/33/400 EU Tank
| 1600/33/440 EU | 1600/33/400 EU Tank
| 1600/33/690 EU | 1600/33/400 EU Tank
| 1600/33/800 EU | 1600/33/400 EU Tank
| 2000/33/415 EU | 2000/33/400 EU Tank
| 2000/33/400 EU | 2000/33/400 EU Tank
| 2000/33/440 EU | 2000/33/400 EU Tank
| 2000/33/690 EU | 2000/33/400 EU Tank
| 2000/33/800 EU | 2000/33/400 EU Tank
| 2500/33/415 EU | 2500/33/400 EU Tank
| 2500/33/400 EU | 2500/33/400 EU Tank
| 2500/33/440 EU | 2500/33/400 EU Tank
| 2500/33/690 EU | 3150/33/415 EU Tank
| 2500/33/800 EU | 2500/33/400 EU Tank
| 3150/33/415 EU | 3150/33/415 EU Tank
| 3150/33/400 EU | 3150/33/415 EU Tank
| 3150/33/440 EU | 3150/33/415 EU Tank
| 3150/33/690 EU | 3150/33/415 EU Tank
| 3150/33/800 EU | 3150/33/415 EU Tank
Standard Aluminium EU2021 Radiators | 1000/33/415 EU AL | 1250/33/400 EU AL Tank
| 1000/33/400 EU AL | 1250/33/400 EU AL Tank
| 1000/33/440 EU AL | 1250/33/400 EU AL Tank
| 1000/33/690 EU AL | 1250/33/400 EU AL Tank
| 1000/33/800 EU AL | 1250/33/400 EU AL Tank
| 1250/33/415 EU AL | 1250/33/400 EU AL Tank
| 1250/33/400 EU AL | 1250/33/400 EU AL Tank
| 1250/33/440 EU AL | 1250/33/400 EU AL Tank
| 1250/33/690 EU AL | 1250/33/400 EU AL Tank
| 1250/33/800 EU AL | 1250/33/400 EU AL Tank
| 1600/33/415 EU AL | 2000/33/400 EU AL Tank
| 1600/33/400 EU AL | 2000/33/400 EU AL Tank
| 1600/33/440 EU AL | 2000/33/400 EU AL Tank
| 1600/33/690 EU AL | 2000/33/400 EU AL Tank
| 1600/33/800 EU AL | 2000/33/400 EU AL Tank
| 2000/33/415 EU AL | 2000/33/400 EU AL Tank
| 2000/33/400 EU AL | 2000/33/400 EU AL Tank
| 2000/33/440 EU AL | 2000/33/400 EU AL Tank
| 2000/33/690 EU AL | 2000/33/400 EU AL Tank
| 2000/33/800 EU AL | 2000/33/400 EU AL Tank
| 2500/33/415 EU AL | 2500/33/400 EU AL Tank
| 2500/33/400 EU AL | 2500/33/400 EU AL Tank
| 2500/33/440 EU AL | 2500/33/400 EU AL Tank
| 2500/33/690 EU AL | 3150/33/400 EU AL Tank
| 2500/33/800 EU AL | 2500/33/400 EU AL Tank
| 3150/33/415 EU AL | 3150/33/400 EU AL Tank
| 3150/33/400 EU AL | 3150/33/400 EU AL Tank
| 3150/33/440 EU AL | 3150/33/400 EU AL Tank
| 3150/33/690 EU AL | 3150/33/400 EU AL Tank
| 3150/33/800 EU AL | 3150/33/400 EU AL Tank

## Techspecs
LTL TRANSFORMERS (PVT) LTD FRM/DE/16
Transformer Technical Specifications
Customer | EDCO
Project: | EDCO
Contract/Quotation No. | TD EDCO |  | Design No: | 100033415 |  |  | Date: | 2023-04-07
Basic Technical Features |  |  | Unit | Customer Requirements |  | Review by LTL |  | Remarks
1. Capacity |  |  | kVA | 1000 |  | 1000
2. No. of Units required |  |  | Nos. | 2 |  | 2
3. Frequency |  |  | Hz | 50 |  | 50
4. No. of Phases |  |  |  | 3 |  | 3
5. Primary Voltage |  |  | V | 11000 |  | 11000
6. Tappings |  | 1 |  |  |  | 5%
2 | [5 empty] | 2.5%
3 | [5 empty] | 0%
4 | [5 empty] | -2.5%
5 | [5 empty] | -5%
7. Secondary Voltage (No Load) |  |  | V | 415 |  | 415
8. Vector Symbol |  |  |  | Dyn11 |  | Dyn11
9. Lightning Impulse Withstand Voltage (Secondary/Primary) |  |  | kV |  |  | 170/- |  |  |  |  | 33 kV | 0 | 200 / - | 70 / 3
10. Power Frequency Withstand Voltage (Secondary/Primary) |  |  | kV |  |  | 70 / 3 |  |  |  |  | 33 kV | 1 | 170 / - | 70 / 3
11. Conductor Material (Primary / Secondary) |  |  |  | Al/Al |  | Al/Al
12. Temp. Rise | Windings |  | °C |  |  | 55 |  |  |  |  | 11 kV | 0 | 95 / - | 28 / 3
| Top Oil |  | °C |  |  | 50 |  |  |  |  | 7.2 kV | 0 | 75 / - | 28 / 3
13. Efficiency at 100% load (P.F = 0.8) |  |  | % |  |  | 99.999 |  |  |  |  | 7.2 kV | 0 | 60 / - | 20 / 3
14. Voltage regulation at 100% load (P.F = 0.8) |  |  | % |  |  | 3.0612 |  |  |  |  | Custom Choise
15. No Load current |  |  | % |  |  | 0.83 |  | IEC Tolerances Applicable
16. Method of cooling | [5 empty] | ONAN
17. No load loss |  |  | W |  |  | 6.33 |  | IEC Tolerances Applicable
18. Load loss |  |  | W |  |  | 2.04 |  | IEC Tolerances Applicable
19. Impedance voltage |  |  | % |  |  | 6.61 |  | IEC Tolerances Applicable
20. Sound level |  |  | dB |  |  | 55
21. Dimensions
| Length |  | mm |  |  | 1844 |  | Approximately
| Width |  | mm |  |  | 1270 |  | Approximately
| Height |  | mm |  |  | 1927 |  | Approximately
22.Total Weight |  |  | kg |  |  | 4360 |  | Approximately
23.Oil Weight |  |  | kg |  |  | 1210 |  | Approximately
24.Un-tanking Weight |  |  | kg |  |  | 2360 |  | Approximately
25. Availabilty of Cable box in Primary side, Y/N | [5 empty] | N |  |  | Y
26. Availabilty of Cable box in Secondary side, Y/N | [5 empty] | N |  |  | N
27. Hermetically sealed/Conservator |  |  |  | Hermetically sealed |  | Hermetically sealed |  |  | Includes in ISD | Hermetically sealed |  | Galvanize & Powder |  |  | RAL6028 | Dark Green | C1
28. Painting Method, Galvanize/Marine paint/Powder |  |  |  | Shot Blast & Powder |  | Shot Blast & Powder |  | C3 |  | Conservator |  | Shot Blast & Marine paint |  |  | RAL9002 | White | C2
29. Unit Colour | [5 empty] | RAL6028 |  | Dark Green |  |  |  | Shot Blast & Powder |  |  | RAL7032 | Pebble Grey | C3
30. Service conditions | [14 empty] | RAL7033 | Cement Grey | C4
| Max. ambient temp. |  | °C |  |  | 45 | [8 empty] | RAL7031 | Dark Admiralty Grey | C5-I
| Monthly average temp. |  | °C |  |  | 35 | [10 empty] | C5-M
| Yearly average temp. |  | °C |  |  | 25
31. Altitude (Maximum) |  |  | m |  |  | 1000
32. Standard | [5 empty] | IEC60076:2011
33. Protection Available |  | 34. Changes by customer (if any)
ISD (includes protection for oil level, oil temp.,pressure & gas ) | Y
Oil Level Indicator | Includes in ISD |  | Designation |  | Sig. |  |  | Date
Pressure Release Device (Without Contacts) | Y | Designed by: | EE |  |  |  |  | 2023-04-07
Winding Temperature Indicator | N | Reviewed by: | EE |  |  |  |  | 2023-04-07
Bi- Directional Rollers | N | Approved by: | MDC |  |  |  |  | 2023-04-07
Revision No.: 00/25-05-2021
Note on H37: Eranga: =Q!B114
Note on H38: Eranga: =Q!B115
Note on H39: Eranga: =Q!B116
Note on H40: Eranga: =Q!B117
Note on H41: Eranga: =Q!B118
Note on H42: Eranga: =Q!B120

## DDOS
LTL TRANSFORMERS (PVT.) LTD. FRM/DE/01
DESIGN DATA OUTPUT SHEET
CORE DETAIL |  | B (T) : 1.700 | L (mm) : 92 |  |  | WT. (Kg) |  | L | #REF! | #REF!
V/T : 14.975 | GRADE : 23ZDKH | C - C (mm) : 513 | #VALUE! |  |  |  |  | W1 | #REF! | #REF!
AREA : 396.8 cm2 |  | W - H (mm) : 867 | A (mm) : 241 | H (mm) : 190 |  | 673.1
|  |  |  | T1 / T2 / T3 / T4 (mm) : 180 / 160 / 140 / 120 |  | 426.3 / 255.5 / 140.3 / 87.3
WINDING TYPE |  | LV |  |  | HV
VOLTS (L/PH) V |  | 415 / 239.6 |  |  | 33000 / 33000
CURRENT (L/PH) A |  | 1391.205 / 1391.205 |  |  | 17.495 / 10.101
CONNECTION |  | yn |  |  | D
TEST (PF / IMP.) kV |  | 3 / - |  |  | 70 / 170 |  |  |  | 70 / 200 | 33 kV
TURNS |  | #VALUE! |  |  | 2314 / 2204 |  |  |  | 70 / 170 | 33 kV |  | L | 2204 | 5 | 12
LAYERS |  | #VALUE! |  |  | 20 |  |  |  | 28 / 75 | 11 kV
TURNS / LAYER |  | #VALUE! |  |  | 120.00/ 34.00 * |  |  |  | 20 / 60 | 7.2 kV
INSULATION |  | (0.25 + 0.25 SL x 838) DDP Between Layers |  |  | (0.15 + 0.25 SL x 838) DDP Between Layers |  |  |  | 3 / - | LV
(0.15 + 0.25 + 0.25 SL x 838) DDP Between Layers
1 & 2 , 13 & 14 , 14 & 15
EDGE STRIP (mm) |  | 18 x 0.25mm |  |  | 45 x 0.25mm
COOLING DUCT |  | Full Cooling Duct Between Layers 8 & 9 (838 x 920 mm) |  |  | Full Cooling Duct Between Layers 10 & 11 (838 x 1440 mm)
|  | - |  |  | -
|  | - |  |  | -
COND. SIZE BARE (mm) |  | 800.00 x 0.80 |  |  | 3.000 x 2 |  |  | x 2
COND SIZE COVD. (mm) |  | 810 x 10.8 |  |  | 3.11 x 2
COND. AREA (mm2) |  | 1279.857 |  |  | 14.137
AMPS / mm2 |  | 1.087 |  |  | 0.715
LEAD SIZE (mm) |  | 100.000 / 10.000 |  |  | HD Copper - 3 mm dia paper covered |  | HD Copper - 3 mm dia paper covered
FLEXIBLE SIZE (mm) |  | 100.000 / 10.000 |  |  | HD Copper - 3 mm dia paper covered
RADIALS (mm) |  | 38.03/ 38.03/ 38.03 |  |  | 88.99/ 88.99/ 88.99 |  | 7/1.7 bare copper
I.D/O.D (mm) |  | 196 x 288 / 273 x 364 |  |  | 311 x 402 / 489 x 582 |  | 19/1.35 bare copper | [7 empty] | 196 | 310.065
ELEC./WDG. LGTH. (mm) |  | #VALUE! |  |  | 743.780 / 840.000 | [9 empty] | 287.863 | 401.928
EQ. MEAN DIAM. (mm) |  | 146.2572 |  |  | 228.7693 | [9 empty] | 272.065 | 488.042
MEAN TURN (m) |  | 918.961 |  |  | 1437.4 | [9 empty] | 363.928 | 579.905
WEIGHT TOTAL (Kg) |  | 186.07 |  |  | 438.01 | [9 empty] | 0
RESIST / PH (Ohm) |  | 0.000398 @ 75 C |  |  | 7.7580 @ 75 C
12R + DIR STRAY (W) |  | #VALUE! |  |  | #VALUE!
BUSHING |  | EN 2000 x 4 |  |  | Plug-in Type 36 kV 250 A Interface B x 3
CLEARANCES | CORE / LV : 3.00x 3.00x 7.00 mm |  | LV/HV : | 19.000 mm | HV/HV : 25.000 mm | YOKE/COVER/BASE : 220 / 40 mm
LV INNER TUBE | 2 mm PB + 4.5 mm CD (690 x 1100 mm) |  | STICK BARRIER : | 20 mm {2mm Type B CB + (6+6+4 PB) + 2mm Glue Allowance} x 690 mm x 1000 mm
[9 empty] | Total | Noinal | No. of tap pos | Deviation
TAP | TURNS | LOSSES | CALCULATED | GUARANTEED |  | WEIGHTS (Kg) |  |  | 2314 | 2204 | 5 | 55 | 2094 | 4 | 5
1 | 0 | CAPACITY (kVA) | 1000 | 1000 | LV CU | 152.44
2 | 2094 |  |  |  | HV CU | 380.88
3 | 2149 | CU LOSS (W) | 2529 @ 75 C | 16805 | CU LEAD / BUSBAR | 25.07
4 | 2204 | FE LOSS (W) | #VALUE! | 2990 | TOTAL CU | 558.39
5 | 2204 |  |  |  | CORE | 1532.5
6 | 2259 | TOTAL LOSS (W) | #VALUE! |  | LV INSULATION | 15.2
7 | 2314 | REACTANCE (%) | 4.962 |  | HV INSULATION | 55.01
8 |  | IMPEDANCE (%) | 4.968 | 4.968 | CORE AND WDGS | 2192
9 |  | NO LOAD CURRENT (%) | 0.83 |  | OIL WEIGHT | 1202
10 |  | T. RISE OIL (°C) | 36 | 50 | WEIGHT OF RADIATOR | 386
11 |  | T. RISE WDG. (°C) | 37.5 | 55 | TOTAL WEIGHT | 4166 |  |  | 37.5 | 36.0
12 |  | X/R | 20 |  | EXPANSION OIL VOLUME | 30 L
TANK INSIDE | LENGTH (mm) : 1624 |  |  | WIDTH (mm) : | 730 | HEIGHT (mm) : 1507
[5 empty] | CORRUG. L.S DEPTH (mm) : 260 | NO.: 16
HEIGHT OF RADIATOR : |  | 1300 |  |  | CORRUG. S.S DEPTH (mm) : 100 | NO.: 10
NUMBER OF RADIATORS : |  |  | CENTER LENGTH OF THE RADIATOR (mm) :
NUMBER OF ELEMENTS PER RADIATOR : |  |  | TYPE OF RADIATOR : |  |  |  | CENTERED
OFF CENTERED
RATING DETAILS
kVA | 1000 | VECTOR | Dyn11 | COOLING | ONAN | CONTINUOUS : Y
PHASE | 3 | Hz | 50 | VOLTAGE RATIO : 137.73 |  | TYPE OF UNIT : Hermetically sealed | Hermetically sealed
TAPPINGS ON HV |  | ABOVE NOMINAL : | 2 | IN STEPS OF : 2.5 %
|  | BELOW NOMINAL : | 2 | TAP CHANGER TYPE : HR 7A3.335 (30kV 30A 100mm 5 Pos)
SPECIAL ACCESSORIES: |  | ISD
STANDARD : IEC 60076:2011
CUSTOMER | : EDCO |  |  | DESIGNED | : | DATE :
DESIGN NO | : 100033415 |  |  | Q.C.M. | : | DATE :
CONTRACT NO : | : TD EDCO |  |  | AUTHORIZED | : | DATE :
Revision:02/01-07-2009
ISD / HV Enclosure 36kV 250A Interface B Plug-in Type Bushings / LV DT3150 Cable Box (6 runs per phase & neutral)

## DDOSnew
LTL TRANSFORMERS (PVT.) LTD. FRM/DE/01
DESIGN DATA OUTPUT SHEET
GENERAL SPECIFICATIONS
kVA |  |  | 1000 |  | VECTOR | Dyn11
PHASE |  |  | 3 |  | Hz | 50
WINDING TYPE |  | LV |  |  | HV
CONDUCTOR MATERIAL |  | Al |  |  | Al
VOLTS (L/PH) V |  | 415 / 239.6 |  |  | 33000 / 33000
CURRENT (L/PH) A |  | 1391.205 / 1391.205 |  |  | 17.495 / 10.101
CONNECTION |  | yn |  |  | D
MAJOR PRODUCT DATA
LEAD SIZE (mm) |  | 100.000 / 10.000 |  |  | HD Copper - 3 mm dia paper covered
FLEXIBLE SIZE (mm) |  | 100.000 / 10.000 |  |  | HD Copper - 3 mm dia paper covered
BUSHING |  | EN 2000 x 4 |  |  | Plug-in Type 36 kV 250 A Interface B x 3
OIL WEIGHT (kg) |  | 1202
EXPANSION OIL VOLUME (L) |  | 30
TANK INSIDE | LENGTH(mm) | 1624
| WIDTH(mm) | 730
| HEIGHT(mm) | 1507
HEIGHT OF RADIATOR(mm) |  | 1300
CORRUG. L.S DEPTH (mm) |  | 260
CORRUG. S.S DEPTH (mm) |  | 100
No. of RIBS |  | 16 / 10
DATA FOR TESTING
RESIST / PH (Ohm) |  | 0.0004179 @ 75 C |  |  | 8.1459 @ 75 C
T. RISE OIL (°C) | CALCULATED | 36
| GUARANTEED | 50
T. RISE WDG. (°C) | CALCULATED | 37.5
| GUARANTEED | 55
DATA FOR TAPPINGS
TAP CHANGER TYPE |  | HR 7A3.335 (30kV 30A 100mm 5 Pos)
IN STEPS OF |  | 2.5 %
ABOVE/ BELOW NOMINAL |  | 2 / 2
SPECIAL ACCESSORIES:
LIST |  | ISD, SAMB, LV Cable box
STANDARD : IEC 60076:2011
CUSTOMER | : EDCO |  |  | DESIGNED | : | DATE : 23/8/2021
DESIGN NO | : 100033415 |  |  | REVIEWED | : | DATE : 23/8/2021
CONTRACT NO : | : TD EDCO |  |  | APPROVED | : | DATE : 23/8/2021
Revision:0/1/6/2021