## R
ta File Name: C:\Us | ers\Kushan\OneDrive | akdhanavi Limited\D | esktop\LTLTrafoDesig | eportVB.dat
* Using Standard Da | ta from Files; Usi | New LTL Core Loss C | alculations ***
TE: 2023.06.14 |  | IQUID TYPE TRANSFOR | MER CALCULATION (Ver | n 6.10.0) |  | Time: 10:10:52
DER : 400033415 | DESIGN: Data Set 1 | ENGINEER: KUSHAN | CUSTOMER NAME | PS Tansania
A - 4000 Liquid | Type ONAN Cooli | 62 C Rise Th | ree Phase 50 Hz | Style Number: Non | e
: 33000 + 2- 2x 2. | 50 % TC: Off-load T | Changer | BIL: 170 (Delt | Line/Coil Amps: |  | 69.982/ 40.404
: 415 |  |  | BIL: 3 (Wye | Line/Coil Amps: | 5 | 564.822/5564.822
------------------- | -------------------- | ----- S T A C K E D | C O R E -------- | --------- Width -- |  | Build ----- Weight -
Core Design.......: | OVAL Mitered | Diagonal Dimension: | 300.000 x 351.095 mm | Step 1: 300.000, |  | 51.095 mm 704.6 kg
Grade/Frame Type..: | 27ZH00 / 3-Leg | Window Height.....: | 890.000 mm | Step 2: 290.000, |  | 77.970 mm 1039.3 kg
INDUCTION.........: | 1.750 Tesla | Center to Center..: | 655.421 mm | Step 3: 260.000, |  | 72.220 mm 863.1 kg
VPT, W/kg, PBase..: | 29.950, 1.225, 1.05 | Gross/Net CSA.....: | 793.1 / 770.9 cm2 | Step 4: 220.000, |  | 54.280 mm 548.9 kg
100 % Exc Current.: | 0.3902 | Weight of Core-Leg: | 2036.9 kg | Step 5: 180.000, |  | 35.880 mm 296.9 kg
Sound/Natural Freq: | 58.2 db / 484 Hz | Weight of Yoke....: | 1463.3 kg | Step 6: 120.000, |  | 34.960 mm 192.8 kg
Peak HV Inrush Cur: | 558 amp | Core Net Weight...: | 3500.0 kg | Step 7: 0.000, |  | 0.000 mm 0.0 kg
Utilization Factor: | 0.9221 | Core Scrap Weight.: | 145.4 kg | Step 8: 0.000, |  | 0.000 mm 0.0 kg
Standard Core No..: | NONE STANDARD | Core Gross Weight.: | 3645.4 kg | Step 9: 0.000, |  | 0.000 mm 0.0 kg
Ovality Factor....: | 1.088 | Use Max Steel Wi | dth (Steps minus 1) | Using Std | S | teel Widths
Core Perimeter....: | 1044.7 mm | Delta Build.......: | 51.1 mm
------------------- | -------------------- | L O W V O L T A | G E W I N D I N G | ------------------ | - | --------------------
Type of Coil......: | CU-Foil | Coil-Length.......: | 840.000 mm | ELECT LENGTH...... | : | 800.000 mm
TURNS PER COIL....: | 1 x 8.0 | Inside Dimensions.: | 307.000 x358.095 mm | Strip-#x#x Wd x Tk | : | 1x1x 800.00 x 3.000
CURRENT DENSITY...: | 2.319 A/mm2 | Outside Dimensions: | 372.421 x423.516 mm | Cond/Lead Weight.. | : | 603.53 / 113.33 kg
|  | Inner Perimeter...: | 1066.7 mm
Cooling Ducts Tk/#: | 4.500 mm / 1.00 | Rad Blds (H,Leg,L): | 32.71/ 32.71/ 32.71 | Lay/Trn/Duc Wts... | : | 10.31/ 0.00/ 1.73
Eff No Cool Ducts.: | HV: 1 Leg: 1 LV: 1 | Axial Allowance...: | 0.000 mm | Total Insul Weight | : | 12.04 kg
Short-Circuit Curr: | 167995 Amp. | Num Support Sticks: | 12
Mean Turn Length..: | 1169.422 mm | Lead: Wd / Tk..: | 100.000 / 20.000 mm | Total Coil Weight. | : | 728.90 kg
Max Turn Lth Buckl: | 2655.562 mm | Bus Bar: Wd / Tk..: | 100.000 / 20.000 mm
|  | Layer Insul Tk....: | 0.400 mm
T-RISE/GRADIENT...: | 60.5/17.9 deg C | Watts/sq m .......: | 1143.851 | Resistance (Coil). | : | 8.2E-050 @ 75 C
Turn CSA .........: | 2400.000 mm2 |  |  | Conductor Dims.... | : | Specified Size
------------------- | -------------------- | I G H V O L T A | G E W I N D I N G | ------------------ | - | --------------------
Type of Coil......: | Layer-Wound Coil | Coil-Length.......: | 840.000 mm | Cond Mec/Elec Lgth | : | 750.000 / 735.600
Conductor.........: | CU-Rectangular | Inside Dimensions.: | 414.421 x 465.516 | Cond-Dim Per Turn. | : | 1x2x 2.700 x 6.700
Turns Tot./Nominal: | 1157/ 1102 | Outside Dimensions: | 632.421 x 683.516 | Cond Area Per Turn | : | 35.08124 mm2
Cooling Ducts Tk/#: | 4.500 mm / 3.00 | Rad Blds (H,Leg,L): | 109.00/109.00/109.00 | HV Conductor Wt... | : | 1905.56 kg
Eff No Cool Ducts.: | HV: 3 Leg: 3 LV: 3 | Add Rad Allowance.: | 0.000 mm | Lay/Trn/Duc Wts... | : | 67.95/ 51.61/ 7.74
Mean Turn Length..: | 1746.6 mm | Layer/Turn Ins Bd.: | 0.650/ 0.500 mm | Insulation Weight. | : | 127.30 kg
LayIns Tk.........: | (19 Full) 0.650 mm | LayIns RB W/OvBld.: | 13.72 mm | Average LayIns Tk. | : | 0.650 mm
CURRENT DENSITY...: | 1.152 A/mm2 | # Sup Pts/Ax All..: | 12 / 1.200 mm | Total Coil Weight. | : | 2032.86 kg
# Lay: Max/Min tpl: | 23# 51.00/ 35.00 * | Axial Sections....: | 1 | Layer-Layer Volts. | : | 3054.9
T-RISE/GRADIENT...: | 50.3/ 8.1 deg C | Watts/sq m .......: | 265.950 | Resistance (Coil). | : | 1.1500 @ 75 C
|  |  |  | Conductor Dims.... | : | Specified Size
------------------- | -------------------- | L E C T R I C A L | C L E A R A N C E | ------------------ | - | --------------------
LV to Core Leg(mm): | 3.50x 3.50x 10.00 | LV Cond to Yoke...: | 45.000 mm | Total HV-LV Offset | : | 50.000 mm
Eff Hi-Lo ElecSpan: | 21.000 mm | Ph-Ph Elec Spacing: | 23.000 mm | Max LV Sup Span... | : | 66.000 mm
HV-HSide/HV-LSide.: | 90.00 / 90.00 mm | HV-Ends...........: | 75.000 mm | Yoke-Case Top/Bot. | : | 280.00 / 41.00 mm
HV Fixed Gap......: | 0.000 mm
-------- BASIS FOR | CALCULATIONS ------- | ------------------- | -- MATERIAL PRICES | USD/KG (17-08-01 | ) | -------------------
Netw.Short Cir.Cap: | 1500.0 MVA | E Rnd Wire: AL/CU.: | 4.56 / 11.73 | Core Cost......... | : | 3.54
Wdg Rise Limit....: | 62.0 deg C | Rect Wire : Al/Cu.: | 5.63 / 7.37 | Turn/Lay/DD Insul. | : | 2.18 / 3.28 / 4.1
Top Oil Rise Limit: | 56.0 deg C | Foil Cond: AL/CU..: | 3.59 / 11.73 | Mineral/Silicone.. | : | 0.98 / 6.12
Max No Load/Load..: | 4570 / 35800 | LME/1000 (CU/AL)..: | 0 / 0 | Case Steel/Cooling | : | 0.78 / 3.83
------------------- | ------------- WEIGHT | DIMENSIONS, AND COO | LING (RADIATORS: MEN | M140 & M141 ) -- | - | --------------------
Active Part Weight: | 6310 kg | Conservator Weight: | 96.94 kg | C&C Dim: Ht/Lgth.. | : | 1490.00/1943.26 mm
Clamp & Brace Wt..: | 631 kg | H-L Barrier Weight: | 48.61 kg | Ele Derating Fac.. | : | 1.000
Silicone Weight...: | 2828 kg | Rads - Weight.....: | 1205 kg | Rads, Elem/rad, Ht | : | 6 14 1300.0 mm
Bus bar/TC Weight.: | 71/ 0 kg | Fixed Radiator | Parameters | Elems Req/Actual.. | : | 71/ 84
Cov/Case & Cooling: | 283/ 2862 kg | Rad C to C Space..: | 1100.00 mm | Rad Element Wd/Tk. | : | 520.00/ 11.40 mm
Total Weight......: | 12985 kg |  |  | Case: Lt/Wd/Ht(mm) | : | 2093.3x 936.1x1811.0
------------------- | -------------------- | ------PRICE & COST | IN USD UNITS ------- | ------------------ | - | --------------------
Core Cost.........: | 12390 | HV / LV Coil Cost.: | 14514/ 8462 | Labor & VOH/Hours. | : | 0 / 0
Case/Cooling Cost.: | 1512/ 4614 | Bracing Cost......: | 492 | Design Matl-Cost.. | : | 61768
Silicone Liquid...: | 17309 | Assy and Misc.....: | 2474 | Variable Cost..... | : | 61768
EVALUATED LOSSES..: | 0 | EVALUATED COST....: | 61768 | RECOMMENDED PRICE. | : | 123536
------------------- | -------------------- | ---------- PERFORMA | NCE DATA ----------- | ------------------ | - | --------------------
HV Wdg DC Losses..: | 5632 Watts | LV Wdg DC Losses..: | 7590 Watts
HV Watts (% Eddy).: | 7248 (22.3) | LV Watts (% Eddy).: | 10273 (20.8) | LV Bus Bar / Stray | : | 1284 / 15225
No Load Losses....: | 4287 Watts | Tot-Ld Watts(%Ed).: | 34030 (59.5) | Total Losses(ONAN) | : | 38317 @ 75 C
Tank Dissipation..: | 5964 Watts | Ele Dissipation...: | 367 Watts | Total Rad Dissip.. | : | 32650 Watts
% X / % R / % Lead: | 7.26/0.85/0.38 % | % Z (HV-LV-Lead)..: | 7.692 % | TOP OIL RISE...... | : | 49.7 deg C
|  | % Z Guaranteed....: | 7.500 %
------------------- | -------------------- | ------------------- | -------------------- | ------------------ | - | --------------------
TES: HV Axial & Ra | d Factors - 1.000, | 900 LV Rad Fact | or - 0.950 OPT | : (Min Evaluated C | o | st )
MARG/MULT.: < | Rise>: Top Oil= 0 H | 0 L= 0 T= 0 <Loss | >: Core= 1.000 BusB= | 1.0 Eddy H= 1.0 | L | = 1.0 Stray= 1.0
CORE: Std(NO | ) Wds(YES) C-C(NO ) | g(NO ), COND: Foil | Tk(NO ), CLEAR: Wd | O ), CASE: Std(NO |  | ) CALC: Sh Cir(YES)
Circuit Load | Factors: HV= 1.000, | LV= 1.000, TV= 1. | 000
Circuit Load | Factors: HV= 1.000, | LV= 1.000, TV= 1. | 000
Using LTL Cor | e Loss Calculation T | nical Standard: < Y | ES >
Using LTL Loa | d Loss Calculation T | nical Standard: < N | O >
Impedance Mod | el: Convensional
Tapping Turns | @.......: 1 - 1157, | - 1129, 3 - 1102, 4 | - 1074, 5 - 1047

## P
| Section | Value | Row No | Column No
| Start | DESIGN: Data Set 1 | 7 | 2
| Core | C O R E -------- | 10 | 4
| LV | L O W V O L T A | 21 | 3
| HV | I G H V O L T A | 33 | 3
| Clearances | L E C T R I C A L | 44 | 3
| Calculations | CALCULATIONS ------- | 48 | 2
| Weights & Dimensions | WEIGHTS, DIMENSIONS | 15 | 3
| Prices | IN USD UNITS ------- | 58 | 4
| Performance data | NCE DATA ----------- | 62 | 4
| Factors | -------------------- | 68 | 4
Start | 0 | 1 | 2 | 3 | 4 | 5 | 6
-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-1 | TE: 2023.06.14 | 0 | IQUID TYPE TRANSFOR | MER CALCULATION (Ver | n 6.10.0) | 0 | Time: 10:10:52
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | DER : 400033415 | DESIGN: Data Set 1 | ENGINEER: KUSHAN | CUSTOMER NAME | PS Tansania | 0 | 0
2 | A - 4000 Liquid | Type ONAN Cooli | 62 C Rise Th | ree Phase 50 Hz | Style Number: Non | e | 0
3 | : 33000 + 2- 2x 2. | 50 % TC: Off-load T | Changer | BIL: 170 (Delt | Line/Coil Amps: | 0 | 69.982/ 40.404
4 | : 415 | 0 | 0 | BIL: 3 (Wye | Line/Coil Amps: | 5 | 564.822/5564.822
5 | ------------------- | -------------------- | ----- S T A C K E D | C O R E -------- | --------- Width -- | 0 | Build ----- Weight -
6 | Core Design.......: | OVAL Mitered | Diagonal Dimension: | 300.000 x 351.095 mm | Step 1: 300.000, | 0 | 51.095 mm 704.6 kg
Core
0 | ------------------- | -------------------- | ----- S T A C K E D | C O R E -------- | --------- Width -- | 0 | Build ----- Weight -
1 | Core Design.......: | OVAL Mitered | Diagonal Dimension: | 300.000 x 351.095 mm | Step 1: 300.000, | 0 | 51.095 mm 704.6 kg
2 | Grade/Frame Type..: | 27ZH00 / 3-Leg | Window Height.....: | 890.000 mm | Step 2: 290.000, | 0 | 77.970 mm 1039.3 kg
3 | INDUCTION.........: | 1.750 Tesla | Center to Center..: | 655.421 mm | Step 3: 260.000, | 0 | 72.220 mm 863.1 kg
4 | VPT, W/kg, PBase..: | 29.950, 1.225, 1.05 | Gross/Net CSA.....: | 793.1 / 770.9 cm2 | Step 4: 220.000, | 0 | 54.280 mm 548.9 kg
5 | 100 % Exc Current.: | 0.3902 | Weight of Core-Leg: | 2036.9 kg | Step 5: 180.000, | 0 | 35.880 mm 296.9 kg
6 | Sound/Natural Freq: | 58.2 db / 484 Hz | Weight of Yoke....: | 1463.3 kg | Step 6: 120.000, | 0 | 34.960 mm 192.8 kg
7 | Peak HV Inrush Cur: | 558 amp | Core Net Weight...: | 3500.0 kg | Step 7: 0.000, | 0 | 0.000 mm 0.0 kg
8 | Utilization Factor: | 0.9221 | Core Scrap Weight.: | 145.4 kg | Step 8: 0.000, | 0 | 0.000 mm 0.0 kg
9 | Standard Core No..: | NONE STANDARD | Core Gross Weight.: | 3645.4 kg | Step 9: 0.000, | 0 | 0.000 mm 0.0 kg
10 | Ovality Factor....: | 1.088 | Use Max Steel Wi | dth (Steps minus 1) | Using Std | S | teel Widths
11 | Core Perimeter....: | 1044.7 mm | Delta Build.......: | 51.1 mm | 0 | 0 | 0
12 | ------------------- | -------------------- | L O W V O L T A | G E W I N D I N G | ------------------ | - | --------------------
13 | Type of Coil......: | CU-Foil | Coil-Length.......: | 840.000 mm | ELECT LENGTH...... | : | 800.000 mm
14 | TURNS PER COIL....: | 1 x 8.0 | Inside Dimensions.: | 307.000 x358.095 mm | Strip-#x#x Wd x Tk | : | 1x1x 800.00 x 3.000
LV
1 | ------------------- | -------------------- | L O W V O L T A | G E W I N D I N G | ------------------ | - | --------------------
2 | Type of Coil......: | CU-Foil | Coil-Length.......: | 840.000 mm | ELECT LENGTH...... | : | 800.000 mm
3 | TURNS PER COIL....: | 1 x 8.0 | Inside Dimensions.: | 307.000 x358.095 mm | Strip-#x#x Wd x Tk | : | 1x1x 800.00 x 3.000
4 | CURRENT DENSITY...: | 2.319 A/mm2 | Outside Dimensions: | 372.421 x423.516 mm | Cond/Lead Weight.. | : | 603.53 / 113.33 kg
5 | 0 | 0 | Inner Perimeter...: | 1066.7 mm | 0 | 0 | 0
6 | Cooling Ducts Tk/#: | 4.500 mm / 1.00 | Rad Blds (H,Leg,L): | 32.71/ 32.71/ 32.71 | Lay/Trn/Duc Wts... | : | 10.31/ 0.00/ 1.73
7 | Eff No Cool Ducts.: | HV: 1 Leg: 1 LV: 1 | Axial Allowance...: | 0.000 mm | Total Insul Weight | : | 12.04 kg
8 | Short-Circuit Curr: | 167995 Amp. | Num Support Sticks: | 12 | 0 | 0 | 0
9 | Mean Turn Length..: | 1169.422 mm | Lead: Wd / Tk..: | 100.000 / 20.000 mm | Total Coil Weight. | : | 728.90 kg
10 | Max Turn Lth Buckl: | 2655.562 mm | Bus Bar: Wd / Tk..: | 100.000 / 20.000 mm | 0 | 0 | 0
11 | 0 | 0 | Layer Insul Tk....: | 0.400 mm | 0 | 0 | 0
12 | T-RISE/GRADIENT...: | 60.5/17.9 deg C | Watts/sq m .......: | 1143.851 | Resistance (Coil). | : | 8.2E-050 @ 75 C
13 | Turn CSA .........: | 2400.000 mm2 | 0 | 0 | Conductor Dims.... | : | Specified Size
HV
2 | ------------------- | -------------------- | I G H V O L T A | G E W I N D I N G | ------------------ | - | --------------------
3 | Type of Coil......: | Layer-Wound Coil | Coil-Length.......: | 840.000 mm | Cond Mec/Elec Lgth | : | 750.000 / 735.600
4 | Conductor.........: | CU-Rectangular | Inside Dimensions.: | 414.421 x 465.516 | Cond-Dim Per Turn. | : | 1x2x 2.700 x 6.700
5 | Turns Tot./Nominal: | 1157/ 1102 | Outside Dimensions: | 632.421 x 683.516 | Cond Area Per Turn | : | 35.08124 mm2
6 | Cooling Ducts Tk/#: | 4.500 mm / 3.00 | Rad Blds (H,Leg,L): | 109.00/109.00/109.00 | HV Conductor Wt... | : | 1905.56 kg
7 | Eff No Cool Ducts.: | HV: 3 Leg: 3 LV: 3 | Add Rad Allowance.: | 0.000 mm | Lay/Trn/Duc Wts... | : | 67.95/ 51.61/ 7.74
8 | Mean Turn Length..: | 1746.6 mm | Layer/Turn Ins Bd.: | 0.650/ 0.500 mm | Insulation Weight. | : | 127.30 kg
9 | LayIns Tk.........: | (19 Full) 0.650 mm | LayIns RB W/OvBld.: | 13.72 mm | Average LayIns Tk. | : | 0.650 mm
10 | CURRENT DENSITY...: | 1.152 A/mm2 | # Sup Pts/Ax All..: | 12 / 1.200 mm | Total Coil Weight. | : | 2032.86 kg
11 | # Lay: Max/Min tpl: | 23# 51.00/ 35.00 * | Axial Sections....: | 1 | Layer-Layer Volts. | : | 3054.9
12 | T-RISE/GRADIENT...: | 50.3/ 8.1 deg C | Watts/sq m .......: | 265.950 | Resistance (Coil). | : | 1.1500 @ 75 C
13 | 0 | 0 | 0 | 0 | Conductor Dims.... | : | Specified Size
14 | ------------------- | -------------------- | L E C T R I C A L | C L E A R A N C E | ------------------ | - | --------------------
Clearances
3 | ------------------- | -------------------- | L E C T R I C A L | C L E A R A N C E | ------------------ | - | --------------------
4 | LV to Core Leg(mm): | 3.50x 3.50x 10.00 | LV Cond to Yoke...: | 45.000 mm | Total HV-LV Offset | : | 50.000 mm
5 | Eff Hi-Lo ElecSpan: | 21.000 mm | Ph-Ph Elec Spacing: | 23.000 mm | Max LV Sup Span... | : | 66.000 mm
6 | HV-HSide/HV-LSide.: | 90.00 / 90.00 mm | HV-Ends...........: | 75.000 mm | Yoke-Case Top/Bot. | : | 280.00 / 41.00 mm
7 | HV Fixed Gap......: | 0.000 mm | 0 | 0 | 0 | 0 | 0
8 | -------- BASIS FOR | CALCULATIONS ------- | ------------------- | -- MATERIAL PRICES | USD/KG (17-08-01 | ) | -------------------
9 | Netw.Short Cir.Cap: | 1500.0 MVA | E Rnd Wire: AL/CU.: | 4.56 / 11.73 | Core Cost......... | : | 3.54
10 | Wdg Rise Limit....: | 62.0 deg C | Rect Wire : Al/Cu.: | 5.63 / 7.37 | Turn/Lay/DD Insul. | : | 2.18 / 3.28 / 4.1
Calculations
4 | -------- BASIS FOR | CALCULATIONS ------- | ------------------- | -- MATERIAL PRICES | USD/KG (17-08-01 | ) | -------------------
5 | Netw.Short Cir.Cap: | 1500.0 MVA | E Rnd Wire: AL/CU.: | 4.56 / 11.73 | Core Cost......... | : | 3.54
6 | Wdg Rise Limit....: | 62.0 deg C | Rect Wire : Al/Cu.: | 5.63 / 7.37 | Turn/Lay/DD Insul. | : | 2.18 / 3.28 / 4.1
7 | Top Oil Rise Limit: | 56.0 deg C | Foil Cond: AL/CU..: | 3.59 / 11.73 | Mineral/Silicone.. | : | 0.98 / 6.12
8 | Max No Load/Load..: | 4570 / 35800 | LME/1000 (CU/AL)..: | 0 / 0 | Case Steel/Cooling | : | 0.78 / 3.83
9 | ------------------- | ------------- WEIGHT | DIMENSIONS, AND COO | LING (RADIATORS: MEN | M140 & M141 ) -- | - | --------------------
10 | Active Part Weight: | 6310 kg | Conservator Weight: | 96.94 kg | C&C Dim: Ht/Lgth.. | : | 1490.00/1943.26 mm
11 | Clamp & Brace Wt..: | 631 kg | H-L Barrier Weight: | 48.61 kg | Ele Derating Fac.. | : | 1.000
Weights & Dimensions
-1 | ------------------- | ------------- WEIGHT | DIMENSIONS, AND COO | LING (RADIATORS: MEN | M140 & M141 ) -- | - | --------------------
0 | Active Part Weight: | 6310 kg | Conservator Weight: | 96.94 kg | C&C Dim: Ht/Lgth.. | : | 1490.00/1943.26 mm
1 | Clamp & Brace Wt..: | 631 kg | H-L Barrier Weight: | 48.61 kg | Ele Derating Fac.. | : | 1.000
2 | Silicone Weight...: | 2828 kg | Rads - Weight.....: | 1205 kg | Rads, Elem/rad, Ht | : | 6 14 1300.0 mm
3 | Bus bar/TC Weight.: | 71/ 0 kg | Fixed Radiator | Parameters | Elems Req/Actual.. | : | 71/ 84
4 | Cov/Case & Cooling: | 283/ 2862 kg | Rad C to C Space..: | 1100.00 mm | Rad Element Wd/Tk. | : | 520.00/ 11.40 mm
5 | Total Weight......: | 12985 kg | 0 | 0 | Case: Lt/Wd/Ht(mm) | : | 2093.3x 936.1x1811.0
6 | ------------------- | -------------------- | ------PRICE & COST | IN USD UNITS ------- | ------------------ | - | --------------------
7 | Core Cost.........: | 12390 | HV / LV Coil Cost.: | 14514/ 8462 | Labor & VOH/Hours. | : | 0 / 0
8 | Case/Cooling Cost.: | 1512/ 4614 | Bracing Cost......: | 492 | Design Matl-Cost.. | : | 61768
Prices
6 | ------------------- | -------------------- | ------PRICE & COST | IN USD UNITS ------- | ------------------ | - | --------------------
7 | Core Cost.........: | 12390 | HV / LV Coil Cost.: | 14514/ 8462 | Labor & VOH/Hours. | : | 0 / 0
8 | Case/Cooling Cost.: | 1512/ 4614 | Bracing Cost......: | 492 | Design Matl-Cost.. | : | 61768
9 | Silicone Liquid...: | 17309 | Assy and Misc.....: | 2474 | Variable Cost..... | : | 61768
10 | EVALUATED LOSSES..: | 0 | EVALUATED COST....: | 61768 | RECOMMENDED PRICE. | : | 123536
11 | ------------------- | -------------------- | ---------- PERFORMA | NCE DATA ----------- | ------------------ | - | --------------------
12 | HV Wdg DC Losses..: | 5632 Watts | LV Wdg DC Losses..: | 7590 Watts | 0 | 0 | 0
13 | HV Watts (% Eddy).: | 7248 (22.3) | LV Watts (% Eddy).: | 10273 (20.8) | LV Bus Bar / Stray | : | 1284 / 15225
Performance data
7 | ------------------- | -------------------- | ---------- PERFORMA | NCE DATA ----------- | ------------------ | - | --------------------
8 | HV Wdg DC Losses..: | 5632 Watts | LV Wdg DC Losses..: | 7590 Watts | 0 | 0 | 0
9 | HV Watts (% Eddy).: | 7248 (22.3) | LV Watts (% Eddy).: | 10273 (20.8) | LV Bus Bar / Stray | : | 1284 / 15225
10 | No Load Losses....: | 4287 Watts | Tot-Ld Watts(%Ed).: | 34030 (59.5) | Total Losses(ONAN) | : | 38317 @ 75 C
11 | Tank Dissipation..: | 5964 Watts | Ele Dissipation...: | 367 Watts | Total Rad Dissip.. | : | 32650 Watts
12 | % X / % R / % Lead: | 7.26/0.85/0.38 % | % Z (HV-LV-Lead)..: | 7.692 % | TOP OIL RISE...... | : | 49.7 deg C
13 | 0 | 0 | % Z Guaranteed....: | 7.500 % | 0 | 0 | 0
Factors
8 | ------------------- | -------------------- | ------------------- | -------------------- | ------------------ | - | --------------------
9 | TES: HV Axial & Ra | d Factors - 1.000, | 900 LV Rad Fact | or - 0.950 OPT | : (Min Evaluated C | o | st )
10 | MARG/MULT.: < | Rise>: Top Oil= 0 H | 0 L= 0 T= 0 <Loss | >: Core= 1.000 BusB= | 1.0 Eddy H= 1.0 | L | = 1.0 Stray= 1.0
11 | CORE: Std(NO | ) Wds(YES) C-C(NO ) | g(NO ), COND: Foil | Tk(NO ), CLEAR: Wd | O ), CASE: Std(NO | 0 | ) CALC: Sh Cir(YES)
12 | Circuit Load | Factors: HV= 1.000, | LV= 1.000, TV= 1. | 000 | 0 | 0 | 0
13 | Circuit Load | Factors: HV= 1.000, | LV= 1.000, TV= 1. | 000 | 0 | 0 | 0
14 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | Using LTL Cor | e Loss Calculation T | nical Standard: < Y | ES > | 0 | 0 | 0
16 | Using LTL Loa | d Loss Calculation T | nical Standard: < N | O > | 0 | 0 | 0
17 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Q
MARGINS
Core Loss | 10
Cu Loss | 10
No Load Current | 30
Total Weight | 100
Material Name in MM | Margin (%)
Fin Radiators | 0 | 0 |  | 2.5
| 0 | 0 |  | 2.5
Panel Type Radiators | 0 | 0 |  | 2.5 |  |  | Removable
Cover+Base+Flange | 0 | 0 |  | 2.5
Steel (Total) | 0 | 0 |  | 2.5
Wooden Total | 0 | 0 |  | 2.5
Core steel | 0 | 0 |  | 2.5
Oil | 0 | 0 |  | 2.5
Copper Foil | 0 | 0 |  | 2.5
Round Copper | 0 | 0 |  | 2.5
Copper Bus Bar | 0 | 0 |  | 2.5
Rectangular Copper | 0 | 0 |  | 2.5
DDP-Double Layer | 0 | 0 |  | 2.5
0.15 DDP-Single Layer | 0 | 0 |  | 2.5
0.25 DDP-Single Layer | 0 | 0 |  | 2.5
Strip Insulation | 0 | 0 |  | 2.5
Corrugator Boards- 9.0x2.0 mm | 0 | 0 |  | 2.5
LV Strip | 0 | 0 |  | 2.5
HV Strip | 0 | 0 |  | 2.5
Galvanizing | 0 | 0 |  | 2.5
Primer Paint & Thinner | 0 | 0 |  | 2.5
Powder Paint | 0 | 0 |  | 2.5
Rectangular Copper
ELECTRICAL DATA
TYPE | Panel type |  |  | Rads | Rads - Weight.....:
| Conservator Type |  |  | Conservator | Conservator Weight:
| N | N
Hermetically Sealed
Conservator Type
Fin Radiator
Panel type
Y
N
kVA | 4000 | 3 | 13 |  |  |  |  | Tap Wire | Area | Ph density | Line Density | ph (kg) | line (kg)
HV VOLTS | 33000 | 1 | 9 | 18 |  |  |  | 3 | 7.0686 | 5.716 | 9.9004 | 0 | 0
LV VOLTS | 415 | 1 | 7 |  |  |  |  | 7/1.7 | 15.8886 | 2.543 | 4.4045 | 13 | 0
LV Coil current | 5564.822 | 8 | 16 | 564.822/5564.822 |  | 1 | 2 | 19/1.35 | 27.1964 | 1.4856 | 2.5732 | 0 | 4.3333
LV line current | 5564.822 | [6 empty] | Choise |  | 2.543 | 2.5732
LV Coil current density | 2.319 | 7
: 33000 + 2- 2x 2. | [7 empty] | Capacity | Tapping | Barrier DDP
HV coil current | 40.404 | 14 | 8 | 69.982/ 40.404 |  | Closest capacity | 4000 | 100 | 3 | 0.5
HV line current | 69.982 |  |  |  |  | Tapping Weight | #N/A | 160 | 3 | 0.5
[8 empty] | 250 | 4 | 0.75
HV voltage (kV) | 33 | [6 empty] | 400 | 4 | 1
Basic Insulation Level | 170 | 4 | 10 |  |  |  |  | 630 | 5 | 1.5
%X | 7.26 | 16 | 10 | 5 | 7.26/0.85/0.38 % | % X / % R / % Lead: |  | 800 | 5 | 2
%R | 0.85 | [6 empty] | 1000 | 6 | 2.5
Frequency | 50 | 5 | 18 |  |  |  |  | 1250 | 6 | 3.5
Phases | 3 | ree | [5 empty] | 1600 | 7 | 4.5
Tappings |  | 9 | 12 | 18 |  |  |  | 2000 | 7 | 5.5
+ | 2 | [6 empty] | 2500 | 8 | 6.5
- | -2 | 2 | [5 empty] | 3150 | 13 | 7.5
Steps | 2.5 | 4 | 5
| 5% | 2 | 1
| 2.5% | 1 | 2
| 0% | 0 | 3
| -2.5% | -1 | 4
| -5% | -2 | 5
| - | 0
| - | 0
| - | 0
| - | 0
Vector Group
LV | yn |  | yn
HV | D |  | D
Dyn
Dyn11
Temp. Rise Windings | 60 | 12 | 60
Temp. Rise Top oil | 55 | 11 | 55
% impedence | 7.7 | 7.692 % | % Z (HV-LV-Lead)..: |  | 7.692 | #VALUE!
Full Load Loss | 35800 | 1.1 | 10273 |  |  | 35800
No Load Loss | 4570 | 1.1 | #VALUE! | #VALUE! |  | 4570 |  |  | 7.6877 | 0.25683
No load Current | 0.3902
Sound level | 59
Core Loss Factor | 1 | 16 | 8
Factor k x sqrt(2) | #VALUE! | #VALUE! | #VALUE!
kVA | % Z | % Z-pu | FL loss | NL loss | PU load | PF | X | sin X | %X | %R | %FE | %Eff | %Reg
4000 | 7.7 | 7.7 | 35800 | 4570 | 1 | 0.8 | 0.6435 | 0.6 | 7.6478 | 0.895 | 0.11425 | 98.7542 | 5.4604
DIMENSIONS
CASE
Case-Length | 2093 | 14 | 7 | 20
Case-Width | 936
Case-Height | 1811
HEIGHTS |  | WEIGHTS
Conservator | 780 | 109
HV Box | 0 | 0
ISD | 290 | 5
10 NF 250 CD = 372 mm P-4 EN | 310 | 16.95
#N/A | #N/A | #N/A
LV Box | 0 | 0
Height for base skid and cover | 210 | 99.3249
CABLE BOX
No of intakes /Phase (LV) | 4
LV Box Depth | 0 |  |  | Conservator Length | 685
LV Box Width | 0 |  |  | Panel Add. to Length | 650
HV Box Depth | 0 |  |  | Panel Add. to Width | 1300
HV Box Width | 0
WTI Box Depth | 0
Tolerance
Length | 3448 | 20 | 3428
Width | 2256 | 20 | 2236
Height | #N/A | 20 | #N/A
Weight-TOTAL | #N/A | 50 | #N/A
Weight-OIL | 2830 |  | 2830
Weight-ACTIVE PART | 6310 |  | 6310
Weight-Untanking | 6550 | 50 | 6491
Container Arrangement |  | 40' |  |  | 20'
Length |  | 12045 |  |  | 5919
Width |  | 2280 |  |  | 2286
Weight | 100 | 27396 |  |  | 22100
Length/Length |  | 3 | 1 |  | 1 | 1
Length/Width |  | 5 | 0 |  | 2 | 0
Weight | #N/A | #N/A |  | #N/A | #N/A
DESIGN
Design | 400033415 |  |  | DER : 400033415
Date | 2023.06.14 | 5 | 6 | Time: 10:10:52 | IQUID TYPE TRANSFOR |  |  | TE: 2023.06.14
Time | 10:10:52 | [6 empty] | 3
Customer | PS Tansania
WINDING DATA
Coil Length | 840 | 838 | 750 | 735.6 | 800 | 0 | 1
Window height | 890 | 890.000 | 9
Center to center | 656 | 655.421 | 9
Core Type | OVAL
Height from yoke to cover | 280 | 41.00 mm | 41
LV layer insulations thickness | 0.4
INSULATION
LV layer insulations thickness | 0.15 | 0.18 | 10.31 | 100.000 | 0.18
838mm x 0.15 DDP DL | 10.31 | 1 |  |  |  | 0.15 DDP | 0.25 DDP | 0.15 DDP | 0.25 DDP
838mm x 0.15 DDP SL | 0 | 0 |  |  | 0.15 | 1 |  | 1
838mm x 0.25 DDP SL | 0 | 0 |  |  | 0.18 | 1 |  | 1
[5 empty] | 0.25 | 1 |  | 1
[5 empty] | 0.3 | 1 |  | 2
HV layer insulations thickness | 0.65 | 0.65 | 67.95 |  | 0.35 |  | 1 |  | 1
838mm x 0.15 DDP SL | 0 | 0 |  | 0.65 | 0.4 | 0.5 | 0.5 | 1 | 1
838mm x 0.25 DDP SL | 75.45 | 1 |  | 0.65 | 0.45 | 1 |  | 3
[5 empty] | 0.5 |  | 1 |  | 2
HV strip insulations thickness |  |  | 67.95 |  | 0.55 | 0.67 | 0.33 | 2 | 1
(45 - 59.4) x 0.05 mm Strip | 0 | 0 |  |  | 0.6 | 1 |  | 4
(45 - 59.4) x 0.075 mm Strip | 0 | 0 |  |  | 0.65 |  | 1 |  | 2
[5 empty] | 0.7 | 0.75 | 0.25 | 3 | 1
838mm x 0.15 DDP DL | 10.31 |  |  |  | 0.75 |  | 1 |  | 3
838mm x 0.15 DDP SL | 0 |  |  |  | 0.8 | 0.5 | 0.5 | 2 | 2
838mm x 0.25 DDP SL | 75.45 |  |  |  | 0.85 | 0.8 | 0.2 | 4 | 1 | Edge Strips
[5 empty] | 0.9 | 0.25 | 0.75 | 1 | 3 | 8
LV edge strip | 18 |  |  |  | 0.95 |  | 1 |  | 3 | 18
40 | 3.0 | 13 | 19 |  | 1.00 |  | 1 |  | 4 | 27
1169.422 | 8.0 | 3 | 10 | 3 | 1.1 | 0.66667 | 0.33333 | 4 | 2 | 33
| #VALUE! |  |  |  | 1.2 | 1 |  | 8 | 0 | 45
9355.376 | 2.8964 |  |  |  | 1.25 |  | 1 | 0 | 4
18 | 0.25 |  |  |  | 1.3 | 0.67 | 0.33 | 4 | 2
HV edge strip | 45 |  |  |  | 1.4 | 0.75 | 0.25 | 6 | 2
90 | 6.700 | 12 | 18 |  | 1.5 |  | 1 |  | 6
1746.6 | 23 |  |  |  | 1.6 | 0.5 | 0.5 | 4 | 4
40171.8 | 15.9714 |  |  |  | 1.7 | 0.8 | 0.2 | 8 | 2
(45 - 59.4) | 0.25 |  |  |  | 1.8 | 0.25 | 0.75 | 2 | 6
Duct Space |  |  |  |  | 1.9 |  | 1 |  | 6
LV | 1.73 | 19 | 13 | 6 | 2 |  | 1 |  | 8
HV | 7.74 | 19 | 13 | 6 | 2.1 | 0.4 | 0.6 |  | 8
| 9.47 |  |  |  | 2.2 | 0.66667 | 0.33333 | 1 | 8
Corragated Board |  |  |  |  | 2.3 | 0.17 | 0.83 | 2 | 10
| 48.61 | 7 |  |  | 2.45 | 0.23 | 0.77 | 3 | 10
CORE STEEL
Core Steel | Builds(mm) | Weight(kg) | : | . | "(10)" | "m" | *100 | "k" | Weight | Adjusted Build
300 | 52 | 704.6 | 7 | 13 | 52 | 8 | 0 | 19 | 704.6 | #VALUE! |  | 300
290 | 78 | 1039.3 | 7 | 13 | 78 | 8 | 0 | 19 | 1039.3 | 78 |  | 290 | #VALUE! | #VALUE!
260 | 73 | 863.1 | 7 | 13 | 73 | 8 | 0 | 19 | 863.1 | 73 |  | 260 | #VALUE!
220 | 55 | 548.9 | 7 | 13 | 55 | 8 | 0 | 19 | 548.9 | 55 |  | 220 | #VALUE!
180 | 36 | 296.9 | 7 | 13 | 36 | 8 | 0 | 19 | 296.9 | 36 |  | 180
120 | 35 | 192.8 | 7 | 13 | 35 | 8 | 0 | 19 | 192.8 | #VALUE! |  | 120 | 120
0 | 0 | 0 | 7 | 13 | 0 | 7 | 0 | 18 | 0.0 | 0
0 | 0 | 0 | 7 | 13 | 0 | 7 | 0 | 18 | 0.0 | 0
0 | 0 | 0 | 7 | 13 | 0 | 7 | 0 | 18 | 0.0 | 0
TOTAL | 329 | 3645.4 | 3645.4
core steel type | 27ZH00
core steel thickness | 27ZH100
COPPER
LV | CU-foil
AL-foil
CU-layer-rect
HV | CU-round
CU-rectangular
LV Cu
CU-Foil | 800.00 x 3.00 | 19 | 4 | 2
CU-Foil | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| 800.00 x 3.00 | 800 | 3
800.00 x 3.00mm CU-Foil | 603.53 | 603.53
HV Cu
CU-Rectangular | 2.700 x 6.700 | 18 | 12 | 4 | 2 | 2
6.700
2.700 x 6.700mm CU-Rectangular | 1905.56 | 1905.56
Flat Cu
LV Leads | 113.33 | 8 | 17
Bus Bars | 71
Total | 184.33 |  | 20 | 100 | 18 | 9 | 19
20*100mm | 10.3556
Inhibited Mineral Oil | 3250.5747
STEEL
Steel Density (kg/mm3) | 7.85e-06
Steel Weights | From Program | Calculated
Cover | 283 | 180.8442 | 4 | 12
Case + Cooling | 2862
Case | 1657 | 773.2924
Clamps | 631 | 212.5849 | 5
Conservator | 96.94 | 45.216 | 7
| 2668 | 1212
2668
Radiator Weights
Fin Type Radiators | 0 | 7 | #VALUE!
Panel Type Radiators | 1205 | 6
1205
1205
Galvanize | 3241.94
Steel Channel
MS Ch 76x38x6 , L= 2083mm | 840
MS Ch 100x50x6 , L= 2083mm | 1128
MS Ch 127x64x6 , L= 2083mm | 1458
MS Ch 152x76x6 , L= 2083mm | 1752
MS Ch 200x75x9 , L= 2083mm | 2988
6mm MS Plate 2083x390x6mm | 2340
Base Skid
50x50x6 AI | 50 | 564
76x38x6 MS Channel | 76 | 840 |  | 400 upto including
100x50x6 MS Channel | 100 | 1128 |  | 1000 upto inc
152x152x10 H Iron | 152 | 4360 |  | 2500
250x75x9 MS Channel | 200 | 2988 |  | >2500
| Dimensions |  |  | MS Plate Arrangement-I |  |  | MS Plate Arrangement-II |  |  |  |  | WEIGHT
MS Sheet -Length | 2440
MS Sheet -Width | 1220
| Thickness | Width | Length | L/L | W/W | Nos | L/W | W/L | Nos | Nos of transformer | Required Nos
Cover plate | 10 | 996 | 2313 | 1 | 1 | 1 | 2 | 0 | 0 | 1 | 1 | 180.8442
Base | 6 | 2253 | 936 | 2 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 99.3249
Conservator | 4 | 1200 | 1200 | 2 | 1 | 2 | 2 | 1 | 2 | 2 | 1 | 45.216
Nos of Sheets
Tank | 6 | 1811 | 6360.9 | 2 | 6 | 6 |  |  |  |  | 6 | 542.5727
| Thickness | Width | Length | Description | Qty | CSA | WEIGHT
Stay rod | 19 | - | 1606 | 3/4 inch BS Rod | 8 | 284
Tie Rod | 19 | - | 505 | 3/4 inch BS Rod | 8 | 284
Flange Long side | 10 | 80 | 2253 | 80x80x10 Angle Iron | 2 | 1500 | 53.0581
Flange Short side | 10 | 80 | 936 | 80x80x10 Angle Iron | 2 | 1500 | 22.0428 |  |  |  | cons
Traverse-Horizontal | 20 | 150 | 329 | 150x20 Flat Iron | 2 | 3000 | 15.4959
Traverse-Vertical | 20 | 150 | 330 | 150x20 Flat Iron | 2 | 3000 | 15.543
Foot | 20 | 150 | 605 | 150x20 Flat Iron | 2 | 3000 | 28.4955
Base Skid | - | 200 | 1200 | 250x75x9 MS Channel | 2 | 2988 | 56.2939
Steel Channel | 6 | 390 | 2083 | 6 mm MS Plate | 4 | 2340 | 153.0505
Wooden cross cut height | 10 | 89 | 1650 | 0 | 0 | 890
Wooden clamp height | 270 | 50 | 2073 | 0 | 0 | 13500
COOLING
Panel Radiators | YES | 71
6 14 1300.0 mm | 2 | 5 | 10
No of radiators | 6
Elements/radiator | 14
Center to center distance | 1300
Depth of a radiator | 650
Width of radiator flange | 150
Radiator width | 520
Distance bet 2 radiators | 80
Offset for off-central type | 131
PANEL TYPE RADS | LV | HV | Cons. Side | Other Side | Length Addition | Width Addition
1 | 1 | 0 | 0 | 0 | 0 | 650
1 | 2 | 0 | 0 | 0 | 0 | 650
3 | 2 | 1 | 0 | 0 | 0 | 1300
4 | 2 | 2 | 0 | 0 | 0 | 1300
5 | 2 | 2 | 1 | 0 | 650 | 1300
6 | 2 | 2 | 2 | 0 | 650 | 1300
7 | 2 | 2 | 2 | 1 | 1300 | 1300
8 | 2 | 2 | 2 | 2 | 1300 | 1300
Fin depth-long side | 0 | #VALUE! | #VALUE!
Fin depth-short side | 0
Fin height | 0 | #VALUE!
Fin Thickness | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Labour Hours |  |  | 0 | #REF!
| 10 |  |  | #REF!
| 10 |  |  | 0
#REF!
ACCESSORIES
HV Bushings | 10 NF 250 CD = 372 mm P-4 EN |  |  | 310 | 3 | 5.65 | 3
170 | 36 | 170 | 250 |  |  |  | 4
Selection | Voltage (kV) | BIL (kV) | Current (A) | Height (mm) | Description | Weight (kg)
1 | 12 | 75 | 250 | 310 | 10 NF 250 CD = 372 mm P-4 EN | 5.65
0 | 12 | 75 | 630 | 342 | 10 NF 630 | 8
0 | 12 | 75 | 250 | 150 | 1M (B9722) | 5
0 | 24 | 125 | 250 | 310 | 24 NF 250 P3 CD = 605 mm | 5.65
0 | 24 | 125 | 250 | 150 | Plug-in Type 24 kV 250 A Interface B | 5
0 | 24 | 125 | 630 | 150 | Plug-in Type 24 kV 630 A Interface C | 6.5
0 | 36 | 200 | 250 | 520 | 30 NF 250 CD = 900 mm P-3 EN | 9.35
0 | 36 | 200 | 250 | 520 | 30 NF 250 CD = 1116 mm | 12.55
0 | 36 | 200 | 250 | 520 | 30 NF 250 CD = 1920 mm | 12.55
1 | 36 | 170 | 250 | 150 | Plug-in Type 36 kV 250 A Interface B | 5
0 | 36 | 170 | 630 | 150 | Plug-in Type 36 kV 630 A Interface C | 6.5
0 | 52 | 250 | 1000 | 150 | Plug-in Type 52 kV 1000 A Interface F | 8
0 | 42 | 200 | 250 | 500 | 40 NF 250 | 15
0 | 52 | 250 | 1000 | 730 | 52 NF 1000 CD = 1430 mm | 35.2
LV Bushings | #N/A |  | #N/A | #N/A | 8 |  | 3
5564.822 | 1 | 0 |  |  |  |  | 4
Selection | Voltage (kV) | Current (A) | Height (mm) | Weight (kg) | Description |  | 6
8
0 | 1 | 250 | 120 | 0.43 | EN 250 | 250
0 | 1 | 630 | 165 | 1.16 | EN 630 | 630
0 | 1 | 1250 | 177 | 2.73 | EN 1250 | 1250
0 | 1 | 2000 | 240 | 6.24 | EN 2000 | 2000
0 | 1 | 2500 | 177 | 2.73 | EN 1250 | 1250
0 | 1 | 3150 | 250 | 8.45 | EN 3150 | 3150
0 | 1 | 4000 | 240 | 6.24 | EN 2000 | 2000
0 | 1 | 6300 | 250 | 8.45 | EN 3150 | 3150
0 | 12 | 250 | 310 | 5.65 | 10 NF 250 | 250
0 | 12 | 630 | 310 | 8 | 10 NF 630 | 630
0 | 12 | 250 | 150 | 5 | 1M (B9722) | 250
0 | 24 | 250 | 150 | 5 | Plug-in Type 24 kV 250 A Interface B | 250
0 | 24 | 630 | 150 | 6.5 | Plug-in Type 24 kV 630 A Interface C | 630
Tap selector | HM 25.44.885 (30kV 63A 131mm 5 Pos) | [5 empty] | 0
1 | 30 | 63 | 200 | 5 |  |  | 1
Selection | Voltage (kV) | Current (A) | BIL (kV) | Positions | Description
0 | 20 | 30 | 95 | 5 | HR 7A3.235 (20kV 30A 100mm 5 Pos)
0 | 20 | 30 | 95 | 7 | HR 7A3.235 (20kV 30A 100mm 7 Pos)
0 | 20 | 63 | 95 | 5 | HM 25.43.885 (20kV 63A 131mm 5 Pos)
0 | 20 | 120 | 95 | 5 | HM 28.43.885 (20kV 120A 131mm 5 Pos)
0 | 20 | 250 | 95 | 5 | HM 28.43.885 (20kV 250A 131mm 5 Pos)
0 | 30 | 30 | 200 | 5 | HR 7A3.335 (30kV 30A 100mm 5 Pos)
0 | 30 | 30 | 200 | 7 | HR 7A3.335 (30kV 30A 100mm 7 Pos)
0 | 30 | 30 | 200 | 5 | HM 23.44.885 (30kV 30A 131mm 5 Pos)
0 | 30 | 30 | 200 | 7 | HM 23.44.885 (30kV 30A 131mm 7 Pos)
1 | 30 | 63 | 200 | 5 | HM 25.44.885 (30kV 63A 131mm 5 Pos)
Valves
PRV T-10K1 1R"
PRV T-50 0.4 BAR
DRAIN VALVE NW 40
AIR RELEASE PLUG
ARES DIN25 DOUBLE FLANGE GATE VALVE
SINGLE FLANGE BALL VALVE 1" NW25S-SS
THROTTLE VALVE FOR RADIATOR NW80 FORMB
BALL VALVE 1" PELGER
GATE VALVE WITH SAMPLING
GATE VALVE WITHOUT SAMPLING
SAMPLING VALVE
BALL VALVE 1" Threaded on both sides
Oil Level Indicators
Magnetic- with 400mm boss
Magnetic- with 200mm boss
4 HOLES PRISMATIC
6 HOLES PRISMATIC
8 HOLES PRISMATIC
FLOATING TYPE
VIAT SO4 - Dial Type with Contacts
VIAT SO6 - Dial Type with Contacts
Cable Boxes | [5 empty] | HV Cable Boxes | Selection | Price | Depth | Width | H above cover | Weight
HV CABLE BOX | 0 |  |  |  |  | Plug-In Cable Box | 0 | 350 | 1052 | 747 | 391 | 100
LV CABLE BOX | 950 |  |  |  |  | 1M Cable Box | 0 | 350 | 862 | 578 | 318 | 57
WTI BOX | 0
CONNECTOR BOX | 0 |  |  |  |  | LV Cable Boxes |  | Price | Depth | Width | H above cover | Weight
HV ENCLOSURE | 0 |  |  |  |  | EN 250 | 0 | 500 | 933 | 770 | 331 | 85
Other Parts | [5 empty] | EN 630 | 0 | 600 | 933 | 770 | 331 | 135
RATING PLATE | [5 empty] | EN 1250 | 0 | 700 | 1085 | 1073 | 386 | 150
PHASE MARKING PLATES | [5 empty] | EN 1250 x 2 | 0 | 750 | 1085 | 1073 | 386 | 180
S/A MOUNTING BRACKET | [5 empty] | EN 2000 | 0 | 800 | 1065 | 1115 | 431 | 200
ISD UNIT | [5 empty] | EN 2000 x 2 | 0 | 850 | 1420 | 1115 | 431 | 230
BREATHER 1KG TYPE A | [5 empty] | EN 3150 | 0 | 900 | 1140 | 1185 | 518 | 300
BREATHER 1KG TYPE B | [5 empty] | EN 3150 x 2 | 1 | 950 | 1495 | 1133 | 518 | 340
BREATHER 1KG TYPE C
BREATHER 2KG | [5 empty] | WTI Box | 0 | 250 | 400 | 700 | 500 | 10
THERMOMETER TEK 16 | [5 empty] | Connector Box | 0 | 150 | 300 | 500 | 300 | 5
THERMOWELL 3/4" BSP | [5 empty] | HV Enclosure | 0 | 250 | 630 | 750 | 400 | 15
THERMOMETER POCKET
GALVANIZED CUP FOR THERMOMETER POCKET
BUCHOLZ RELAY EW712
CONSERVATOR FILLING CAP AL. 2"
T/F WHEEL 7613T00691 |  |  |  | SDF |  | HRC Fuse
T/F WHEEL 7613T00691 |  |  |  | Current | 0 | 0
WINDING TEMP. INDICATOR TD50 (354 01 12X6.0) |  |  |  | 20 | 20A 3KL81113HA10
WINDING TEMP. INDICATOR TD76 (354 01 12X6.0) |  |  |  | 32 | 32A 3KL81213HA10
RTD WTI (PT100) |  |  |  | 63 | 63A 3KL81513HA10
RTD OTI (PT100) |  |  |  | 100 | 100A 3KL82113HA10
CT 3000/2A Oil Immersed (Measuring) Ring Type 15VA/0.5 |  |  |  | 125 | 125A 3KL82213HA10
CT 5000/5A Oil Immersed (Measuring) Ring Type 15VA/0.5 |  |  |  | 160 | 160A 3KL82313HA10
CT 1600/1A 5P20 15VA/0.5 2 Core |  |  |  | 200 | 200A 3KL83113HA10
NCT 400/1A 5P20 15VA |  |  |  | 250 | 250A 3KL83213HA10
NCT 1600/1A 5P20 15VA |  |  |  | 315 | 315A 3KL83313HA10
NCT 2000/1A 5P20 15VA |  |  |  | 400 | 400A 3KL83413HA10
CT TERMINAL BOX (2 TERMINALS) |  |  |  | 500 | 500A 3KL84113HA10
CT TERMINAL BOX (4 TERMINALS) |  |  |  | 630 | 630A 3KL84213HA10
CT TERMINAL BOX (6 TERMINALS) |  |  |  | 800 | 800A 3KL84313HA10
24kV ELBOW CONNECTOR SET (03)
36kV ELBOW CONNECTOR SET (03)
52kV ELBOW CONNECTOR SET (04)
OBO SURGE ARRESTERS
LTL Name Board
Nut, Bolt & 2 Washers (Galvanized) M10 x 40 mm
Split washers for tank cover fixing
M12 bolt, nut, spring washer & lock washer for earthing terminal
Flange Gasket
Wooden Pallete For Packing
Painting |  |  |  |  | Capacity | 2 Coat Sys - DFT 130 |  | 3 Coat Sys - DFT 250
GALVANIZING |  |  | 0 |  | 4000 | Primer (kg) | Powder (kg) | Primer (kg) | Powder (kg)
PRIMER PAINT & THINNER |  |  | 30 |  | 250 | 5 | 6 | 10 | 6
POWDER PAINT (RAL7033) |  |  | 40 |  | 800 | 10 | 15 | 20 | 15 |  | 60
INTERNAL PAINT |  |  | 30 |  | 1250 | 15 | 20 | 30 | 20
[5 empty] | 2000 | 20 | 30 | 40 | 30
Cooling Ducts |  |  |  |  | 2500 | 25 | 30 | 50 | 30
LV No. of Cooling Ducts | 1 |  |  |  | 3150 | 30 | 40 | 60 | 40
LV MTL | 1169.422 |  |  |  | 4000 | 40 | 50 | 70 | 50
LV No. of Layers | 8 |  |  |  | 5000 | 50 | 60 | 80 | 60
LV Cooling duct height | 838
| 0.33 | 4 |  |  | 1/3 Cooling Duct Between Layers 4 & 5 (838 x 390 mm)
| 0.67 | 4 |  |  | 2/3 Cooling Duct Between Layers 4 & 5 (838 x 780 mm)
| 1 | 4 |  |  | Full Cooling Duct Between Layers 4 & 5 (838 x 1170 mm)
| 1.33 | 3 | 5 |  | Full Cooling Duct Between Layers 3 & 4 (838 x 1050 mm) | 1/3 Cooling Duct Between Layers 5 & 6 (838 x 430 mm)
| 1.67 | 3 | 5 |  | Full Cooling Duct Between Layers 3 & 4 (838 x 1050 mm) | 2/3 Cooling Duct Between Layers 5 & 6 (838 x 860 mm)
| 2 | 2 | 5 |  | Full Cooling Duct Between Layers 2 & 3 (838 x 1050 mm) | Full Cooling Duct Between Layers 5 & 6 (838 x 1290 mm)
| 2.33 | 2 | 4 | 6 | Full Cooling Duct Between Layers 2 & 3 (838 x 990 mm) | Full Cooling Duct Between Layers 4 & 5 (838 x 1170 mm) | 1/3 Cooling Duct Between Layers 6 & 7 (838 x 450 mm)
| 2.67 | 2 | 4 | 6 | Full Cooling Duct Between Layers 2 & 3 (838 x 990 mm) | Full Cooling Duct Between Layers 4 & 5 (838 x 1170 mm) | 2/3 Cooling Duct Between Layers 6 & 7 (838 x 900 mm)
| 3 | 2 | 4 | 6 | Full Cooling Duct Between Layers 2 & 3 (838 x 990 mm) | Full Cooling Duct Between Layers 4 & 5 (838 x 1170 mm) | Full Cooling Duct Between Layers 6 & 7 (838 x 1340 mm)
HV No. of Cooling Ducts | 3
HV MTL | 1746.6
HV No. of Layers | 23
HV Cooling duct height | 838
| 0.33 | 11 |  |  | 1/3 Cooling Duct Between Layers 11 & 12 (838 x 580 mm)
| 0.67 | 11 |  |  | 2/3 Cooling Duct Between Layers 11 & 12 (838 x 1160 mm)
| 1 | 11 |  |  | Full Cooling Duct Between Layers 11 & 12 (838 x 1750 mm)
| 1.33 | 9 | 16 |  | Full Cooling Duct Between Layers 9 & 10 (838 x 1570 mm) | 1/3 Cooling Duct Between Layers 16 & 17 (838 x 640 mm)
| 1.67 | 8 | 15 |  | Full Cooling Duct Between Layers 8 & 9 (838 x 1570 mm) | 2/3 Cooling Duct Between Layers 15 & 16 (838 x 1280 mm)
| 2 | 7 | 15 |  | Full Cooling Duct Between Layers 7 & 8 (838 x 1570 mm) | Full Cooling Duct Between Layers 15 & 16 (838 x 1920 mm)
| 2.33 | 6 | 13 | 18 | Full Cooling Duct Between Layers 6 & 7 (838 x 1480 mm) | Full Cooling Duct Between Layers 13 & 14 (838 x 1750 mm) | 1/3 Cooling Duct Between Layers 18 & 19 (838 x 670 mm)
| 2.67 | 6 | 12 | 17 | Full Cooling Duct Between Layers 6 & 7 (838 x 1480 mm) | Full Cooling Duct Between Layers 12 & 13 (838 x 1750 mm) | 2/3 Cooling Duct Between Layers 17 & 18 (838 x 1340 mm)
| 3 | 5 | 11 | 17 | Full Cooling Duct Between Layers 5 & 6 (838 x 1480 mm) | Full Cooling Duct Between Layers 11 & 12 (838 x 1750 mm) | Full Cooling Duct Between Layers 17 & 18 (838 x 2010 mm)
Note on D81: Eranga: VALUE(LEFT(P!C82,FIND(".",P!C82,1)-1))
Note on D82: Eranga: VALUE(LEFT(P!C83,FIND(".",P!C83,1)-1))
Note on B83: Eranga: =ROUNDUP(C79*100,2)
Note on B84: Eranga: =MROUND(D80*C80+2,5)
Note on B85: Eranga: =MROUND(D81*C81/B84+2,5)
Note on C140: Eranga Anuradha Bala: =IF(AND(B47<30000,B46<=400),B134-2,IF(VALUE(B134)<611,B134,MROUND(B134-3,5)))
Note on G153: Eranga: Double foil 0.15 DL x 2
Note on G211: Eranga: Axial Parallel

## Bill of Materials
Bill of Materials
Transformer Type: |  | 4000kVA 33000/415V
Contract No.: |  | 0
Customer: |  | APS Tanzania
No of Transformers: |  | 1
| Material | Description | Unit | Qty | Unit Price | Cost | % | Total Quantity | Per Winding Quantity
| MAJOR MATERIALS |  |  | xxx
1 | Oil | Inhibited Mineral Oil | L | 3250.5747 | 1.3 | 4225.7471 | 5.52% | 3250.5747
2
LV Winding
3 | LV Conductor | 800.00 x 3.00mm CU-Foil | kg | 603.53 | 10.82 | 6530.1946 | 8.531% | 603.53 | 201.1767
4 | Cuponal Bus Bar | 20*100mm | kg | 184.33 | 10.01 | 1845.1433 | 2.41% | 184.33 | 61.4433
5 | DDP Double Layer | 838mm x 0.15 DDP DL | kg | 10.31 | 9.03 | 93.0993 | 0.1216% | 10.31 | 3.4367
6 | DDP Single Layer | 838mm x 0.15 DDP SL | kg | 0 | 5.02 | 0 | 0% | 0 | 0
7 | DDP Single Layer | 838mm x 0.25 DDP SL | kg | 0 | 4.48 | 0 | 0% | 0 | 0
8 | LV Edge Strip | 18 x 0.25mm | kg | 2.8964 | 5.09 | 14.7428 | 0.01926% | 2.8964 | 0.96547
9 | LV Insulation Packet | 4000/33 INLV | Nos. | 3 | 200 | 600 | 0.7838% | 3
10 | [6 empty] | 0% | 0
HV Winding
11 | HV Conductor | 2.700 x 6.700mm CU-Rectangular | kg | 1905.56 | 10.41 | 19836.8796 | 25.91% | 1905.56 | 635.1867
12 | DDP Single Layer | 838mm x 0.15 DDP SL | kg | 0 | 5.02 | 0 | 0% | 0 | 0
13 | DDP Single Layer | 838mm x 0.25 DDP SL | kg | 75.45 | 4.48 | 338.016 | 0.4416% | 75.45 | 25.15
14 | HV Strip Insulation | (45 - 59.4) x 0.075 mm Strip | kg | 0 | 4.89 | 0 | 0% | 0 | 0
15 | HV Edge Strip | (45 - 59.4) x 0.25mm | kg | 15.9714 | 5.09 | 81.2945 | 0.1062% | 15.9714 | 5.3238
16 | HV Insulation Packet | 4000/33 INHV | Nos. | 3 | 650 | 1950 | 2.547% | 3
17
Assembly
18 | HD Copper | 3 mm | kg | 0 | 13.13 | 0 | 0% | 0
19 | Bare Copper | 7/1.7 mm | kg | 13 | 10.01 | 130.13 | 0.17% | 13
20 | Bare Copper | 19/1.35 mm | kg | 4.3333 | 10.01 | 43.3767 | 0.05667% | 4.3333
21 | Copper Flexible | 4000/33 CUFX | Nos. | 4 | 200 | 800 | 1.045% | 4
22 | Timber Packet | 4000/33 TMBC & TMAS | Nos. | 1 | 1200 | 1200 | 1.568% | 1
23 | Insulation Packet | 4000/33 INBC & INAS | Nos. | 1 | 422.1 | 422.1 | 0.5514% | 1
24 | Assembly Packets (Core+Tanking+Dispatch) |  | Nos. | 1 | 110 | 110 | 0.1437% | 1
24 | Shark connectors |  |  |  |  | 0 | 0% | 0
| CORE STEEL |  | kg | 3645.4 | 3.24 | 11811.096 | 15.43% | 3645.4
21 | 27ZH100 | 300mm | kg | 704.6 |  | 0 | 0% | 704.6
22 | 27ZH100 | 290mm | kg | 1039.3 | 0 | 0 | 0% | 1039.3 |  | General Choice
23 | 27ZH100 | 260mm | kg | 863.1 | 0 | 0 | 0% | 863.1 |  | #N/A | 4000/33/415 EU CU | CU
24 | 27ZH100 | 220mm | kg | 548.9 | 0 | 0 | 0% | 548.9
25 | 27ZH100 | 180mm | kg | 296.9 | 0 | 0 | 0% | 296.9 |  | Custom Choice
26 | 27ZH100 | 120mm | kg | 192.8 | 0 | 0 | 0% | 192.8
27 | 0 | 0 | kg | 0 | 0 | 0 | 0% | 0
28 | 0 | 0 | kg | 0 | 0 | 0 | 0% | 0
29 | 0 | 0 | kg | 0 | 0 | 0 | 0% | 0
| STEEL |  |  | xxx | [5 empty] | Special Requirements
30 | Trava, Foot & Clamps |  | kg | 631 | 2.64 | 1665.84 | 2.176% | 631 |  | Cover Plate Thickness
31 | Panel Type Radiators | 1300mm, 14 element/rad, 6rads | kg | 3638.2 | 3.48 | 12660.936 | 16.54% | 3638.2 |  | Base Thickness
32 | Pole Mounting Bracket |  | Nos. |  | 15 | 0 | 0% | 0
33 | [9 empty] | Tank Wall Thickness
| ACCESSORIES |  |  | xxx
HV Bushings
33 | Plug-in Type 36 kV 630 A Interface C |  | Nos. | 3 | 110.22 | 330.66 | 0.432% | 3 |  | Plug-in Type 36 kV 630 A Interface C
34 | HV Cable Lugs |  | Nos. |  | 2.55 | 0 | 0% | 0
| LV Bushings |  |  |  |  | 0 | 0%
35 | EN 3150 |  | Nos. | 8 | 300.71 | 2405.68 | 3.143% | 8 |  | EN 3150
36 | LV Cable Lugs |  | Nos. |  | 2.88 | 0 | 0% | 0
| Tap selector |  |  |  |  | 0 | 0%
37 | HM 25.44.885 (30kV 63A 131mm 5 Pos) |  | Nos. | 1 | 232.43 | 232.43 | 0.3036% | 1 |  | HM 25.44.885 (30kV 63A 131mm 5 Pos)
38
| Valves |  |  |  |  | 0 | 0%
39 | PRV T-10K1 1R" |  | Nos. |  | 9.19 | 0 | 0% | 0
40 | PRV T-50 0.4 BAR |  | Nos. | 1 | 117.88 | 117.88 | 0.154% | 1
41 | DRAIN VALVE NW22 |  | Nos. |  | 14.15 | 0 | 0% | 0
42 | AIR RELEASE PLUG |  | Nos. | 0 | 3.3 | 0 | 0% | 0
43 | ARES DIN25 DOUBLE FLANGE GATE VALVE |  | Nos. |  | 93.525 | 0 | 0% | 0
44 | SINGLE FLANGE BALL VALVE 1" NW25S-SS |  | Nos. |  |  | 0 | 0% | 0
45 | THROTTLE VALVE FOR RADIATOR NW80 FORMB |  | Nos. | 12 | 80.38 | 964.56 | 1.26% | 12
46 | BALL VALVE 1" PELGER |  | Nos. | 1 | 9.19 | 9.19 | 0.01201% | 1
47 | GATE VALVE WITH SAMPLING |  | Nos. | 2 | 81.34 | 162.68 | 0.2125% | 2
48 | GATE VALVE WITHOUT SAMPLING |  | Nos. | 0 |  | 0 | 0% | 0
49 | SAMPLING VALVE |  | Nos. |  |  | 0 | 0% | 0
50 | BALL VALVE 1" Threaded on both sides |  | Nos. | 0 | 9.33 | 0 | 0% | 0
51 | [5 empty] | 0 | 0% | 0
| Oil Level Indicators |  |  |  |  | 0 | 0%
52 | Magnetic- with 400mm boss |  | Nos. | 0 |  | 0 | 0% | 0
53 | Magnetic- with 200mm boss |  | Nos. | 0 | 23.58 | 0 | 0% | 0
54 | 4 HOLES PRISMATIC |  | Nos. | 0 | 10.2201 | 0 | 0% | 0
55 | 6 HOLES PRISMATIC |  | Nos. |  | 12.73 | 0 | 0% | 0
56 | 8 HOLES PRISMATIC |  | Nos. |  | 15.2671 | 0 | 0% | 0
57 | FLOATING TYPE |  | Nos. |  | 15.58 | 0 | 0% | 0
58 | VIAT SO4 - Dial Type with Contacts |  | Nos. | 0 | 104.0936 | 0 | 0%
59 | VIAT SO6 - Dial Type with Contacts |  | Nos. | 1 | 147.35 | 147.35 | 0.1925%
60 | [5 empty] | 0 | 0%
| Cable Boxes |  |  |  |  | 0 | 0%
61 | HV CABLE BOX |  | Nos. | 0 | 450 | 0 | 0% | 0
62 | LV CABLE BOX |  | Nos. | 1 | 3761 | 3761 | 4.913% | 1
63 | WTI BOX |  | Nos. |  | 0 | 0 | 0% | 0
64 | CONNECTOR BOX |  | Nos. |  | 150 | 0 | 0% | 0
65 | HV ENCLOSURE |  | Nos. |  | 0 | 0 | 0% | 0
66
| Other Parts |  |  |  |  | 0 | 0%
67 | RATING PLATE |  | Nos. | 1 | 3.64 | 3.64 | 0.004755% | 1
68 | PHASE MARKING PLATES |  | Nos. | 1 | 1.52 | 1.52 | 0.001986% | 1
69 | S/A MOUNTING BRACKET |  | Nos. | 0 | 14.467 | 0 | 0% | 0
70 | ISD UNIT |  | Nos. |  | 308.6 | 0 | 0% | 0
71 | BREATHER 1KG TYPE A |  | Nos. |  | 16.5 | 0 | 0% | 0
72 | BREATHER 1KG TYPE B |  | Nos. | 0 | 26.0156 | 0 | 0% | 0
73 | BREATHER 1KG TYPE C |  | Nos. | 0 | 17.95 | 0 | 0% | 0
74 | BREATHER 2KG |  | Nos. | 1 | 129.27 | 129.27 | 0.1689% | 1
75 | THERMOMETER TWO CONTACTS |  | Nos. | 0 | 80.38 | 0 | 0% | 0
76 | THERMOWELL 3/4" BSP |  | Nos. |  | 10 | 0 | 0% | 0
77 | THERMOMETER POCKET |  | Nos. | 1 | 2.5 | 2.5 | 0.003266% | 1
78 | GALVANIZED CUP FOR THERMOMETER POCKET |  | Nos. |  | 2.5 | 0 | 0% | 0
79 | BUCHOLZ RELAY EW712 |  | Nos. | 1 | 262.56 | 262.56 | 0.343% | 1
80 | CONSERVATOR FILLING CAP AL. 2" |  | Nos. | 1 | 6.06 | 6.06 | 0.007917% | 1
81 | T/F WHEEL 7613T00691 |  | Nos. |  | 13.45 | 0 | 0% | 0
82 | T/F WHEEL 7613T00691 |  | Nos. |  |  | 0 | 0% | 0
83 | WINDING TEMP. INDICATOR TD50 (354 01 12X6.0) |  | Nos. |  |  | 0 | 0% | 0
84 | WINDING TEMP. INDICATOR TD76 (354 01 12X6.0) |  | Nos. |  |  | 0 | 0% | 0
85 | RTD WTI (PT100) |  | Sets. |  |  | 0 | 0% | 0
86 | RTD OTI (PT100) |  | Sets. |  |  | 0 | 0% | 0
87 | CT 3000/2A Oil Immersed (Measuring) Ring Type 15VA/0.5 |  | Nos. |  | 50 | 0 | 0% | 0
88 | CT 5000/5A Oil Immersed (Measuring) Ring Type 15VA/0.5 |  | Nos. |  | 60 | 0 | 0% | 0
89 | CT 1600/1A 5P20 15VA/0.5 2 Core |  | Nos. |  | 170.1 | 0 | 0% | 0
90 | NCT 400/1A 5P20 15VA |  | Nos. |  | 400 | 0 | 0% | 0
91 | NCT 1600/1A 5P20 15VA |  | Nos. |  | 127.575 | 0 | 0% | 0
92 | NCT 2000/1A 5P20 15VA |  | Nos. |  | 297.675 | 0 | 0% | 0
93 | CT TERMINAL BOX (2 TERMINALS) |  | Nos. |  |  | 0 | 0% | 0
94 | CT TERMINAL BOX (4 TERMINALS) |  | Nos. |  | 77.3035 | 0 | 0% | 0
95 | CT TERMINAL BOX (6 TERMINALS) |  | Nos. |  |  | 0 | 0% | 0
96 | 24kV ELBOW CONNECTOR SET (03) |  | Nos. | 0 |  | 0 | 0% | 0
97 | 36kV ELBOW CONNECTOR SET (03) |  | Nos. | 0 |  | 0 | 0% | 0
98 | 52kV ELBOW CONNECTOR SET (04) |  | Nos. | 0 |  | 0 | 0% | 0
99 | OBO SURGE ARRESTERS |  | Nos. | 0 |  | 0 | 0% | 0
100 | LTL Name Board |  | Nos. | 1 | 7.027 | 7.027 | 0.00918% | 1
101 | Nut, Bolt & 2 Washers (Galvanized) M10 x 40 mm |  | Nos. | 0 | 0.43 | 0 | 0% | 0
102 | Split washers for tank cover fixing |  | Nos. | 0 | 0.43 | 0 | 0% | 0
103 | M12 bolt, nut, spring washer & lock washer for earthing terminal |  | Nos. |  | 178.64 | 0 | 0% | 0
104 | MCCB Box |  | Nos. | 0 | 175 | 0 | 0% | 0
105 | 75A Triple Pole MCCB |  | Nos. |  | 65 | 0 | 0% | 0
105 | HV connectors |  | Nos. | 0 | 20 | 0 | 0% | 0
| Painting |  |  |  |  | 0 | 0%
106 | GALVANIZING |  | kg | 0 | 0.30843 | 0 | 0% | 0
107 | PRIMER PAINT & THINNER |  | kg |  | 9.2 | 0 | 0% | 0
108 | POWDER PAINT (RAL7033) |  | kg |  | 5.26 | 0 | 0% | 0
109 | INTERNAL PAINT |  | kg |  | 7.6837 | 0 | 0% | 0
| 0 |  |  | 0 |  | 0 | 0% | 0
| Major Material |  | $ | * * * |  | 64358.5959 | 84.08% | 64358.5959
| Accessories |  | $ | * * * |  | 8544.007 | 11.16% | 8544.007
| Miscellaneous |  | $ | * * * | 5% | 3645.1301 | 4.762% | 3645.1301
| Total Materials |  | $ | * * * |  | 76547.7331 | #DIV/0! | 76547.7331
Design Engineer
-
Note on L45: Eranga: If different radiator is used, type it here.

## Radiator Choise
Standard Copper EU2021 Radiators | 1000/33/415 EU | 1000/33/415 EU Tank
| 1000/33/400 EU | 1250/33/415 EU Tank
| 1000/33/440 EU | 1250/33/415 EU Tank
| 1000/33/690 EU | 1250/33/415 EU Tank
| 1000/33/800 EU | 1250/33/415 EU Tank
| 1250/33/415 EU | 1250/33/415 EU Tank
| 1250/33/400 EU | 1250/33/400 EU Tank
| 1250/33/440 EU | 1250/33/400 EU Tank
| 1250/33/690 EU | 1250/33/400 EU Tank
| 1250/33/800 EU | 1250/33/400 EU Tank
| 1600/33/415 EU | 1600/33/400 EU Tank
| 1600/33/400 EU | 1600/33/400 EU Tank
| 1600/33/440 EU | 1600/33/400 EU Tank
| 1600/33/690 EU | 1600/33/400 EU Tank
| 1600/33/800 EU | 1600/33/400 EU Tank
| 2000/33/415 EU | 2000/33/400 EU Tank
| 2000/33/400 EU | 2000/33/400 EU Tank
| 2000/33/440 EU | 2000/33/400 EU Tank
| 2000/33/690 EU | 2000/33/400 EU Tank
| 2000/33/800 EU | 2000/33/400 EU Tank
| 2500/33/415 EU | 2500/33/400 EU Tank
| 2500/33/400 EU | 2500/33/400 EU Tank
| 2500/33/440 EU | 2500/33/400 EU Tank
| 2500/33/690 EU | 3150/33/415 EU Tank
| 2500/33/800 EU | 2500/33/400 EU Tank
| 3150/33/415 EU | 3150/33/415 EU Tank
| 3150/33/400 EU | 3150/33/415 EU Tank
| 3150/33/440 EU | 3150/33/415 EU Tank
| 3150/33/690 EU | 3150/33/415 EU Tank
| 3150/33/800 EU | 3150/33/415 EU Tank
Standard Aluminium EU2021 Radiators | 1000/33/415 EU AL | 1250/33/400 EU AL Tank
| 1000/33/400 EU AL | 1250/33/400 EU AL Tank
| 1000/33/440 EU AL | 1250/33/400 EU AL Tank
| 1000/33/690 EU AL | 1250/33/400 EU AL Tank
| 1000/33/800 EU AL | 1250/33/400 EU AL Tank
| 1250/33/415 EU AL | 1250/33/400 EU AL Tank
| 1250/33/400 EU AL | 1250/33/400 EU AL Tank
| 1250/33/440 EU AL | 1250/33/400 EU AL Tank
| 1250/33/690 EU AL | 1250/33/400 EU AL Tank
| 1250/33/800 EU AL | 1250/33/400 EU AL Tank
| 1600/33/415 EU AL | 2000/33/400 EU AL Tank
| 1600/33/400 EU AL | 2000/33/400 EU AL Tank
| 1600/33/440 EU AL | 2000/33/400 EU AL Tank
| 1600/33/690 EU AL | 2000/33/400 EU AL Tank
| 1600/33/800 EU AL | 2000/33/400 EU AL Tank
| 2000/33/415 EU AL | 2000/33/400 EU AL Tank
| 2000/33/400 EU AL | 2000/33/400 EU AL Tank
| 2000/33/440 EU AL | 2000/33/400 EU AL Tank
| 2000/33/690 EU AL | 2000/33/400 EU AL Tank
| 2000/33/800 EU AL | 2000/33/400 EU AL Tank
| 2500/33/415 EU AL | 2500/33/400 EU AL Tank
| 2500/33/400 EU AL | 2500/33/400 EU AL Tank
| 2500/33/440 EU AL | 2500/33/400 EU AL Tank
| 2500/33/690 EU AL | 3150/33/400 EU AL Tank
| 2500/33/800 EU AL | 2500/33/400 EU AL Tank
| 3150/33/415 EU AL | 3150/33/400 EU AL Tank
| 3150/33/400 EU AL | 3150/33/400 EU AL Tank
| 3150/33/440 EU AL | 3150/33/400 EU AL Tank
| 3150/33/690 EU AL | 3150/33/400 EU AL Tank
| 3150/33/800 EU AL | 3150/33/400 EU AL Tank

## Techspecs
LTL TRANSFORMERS (PVT) LTD FRM/DE/16
Transformer Technical Specifications
Customer | Uganda - LMB procurement
Project:
Contract/Quotation No. |  |  | Design No: | 400033415 |  |  | Date: | 2023-06-19
Basic Technical Features |  |  | Unit | Customer Requirements |  | Review by LTL |  | Remarks
1. Capacity |  |  | kVA | 4000 |  | 4000
2. No. of Units required |  |  | Nos. | 1 |  | 1
3. Frequency |  |  | Hz | 50 |  | 50
4. No. of Phases |  |  |  | 3 |  | 3
5. Primary Voltage |  |  | V | 11000 |  | 11000
6. Tappings |  | 1 |  |  |  | 5%
2 | [5 empty] | 2.5%
3 | [5 empty] | 0%
4 | [5 empty] | -2.5%
5 | [5 empty] | -5%
7. Secondary Voltage (No Load) |  |  | V | 420 |  | 420
8. Vector Symbol |  |  |  | Dyn11 |  | Dyn11
9. Lightning Impulse Withstand Voltage (Secondary/Primary) |  |  | kV | 75/- |  | 75/- |  |  |  |  | 33 kV | 0 | 200 / - | 70 / 3
10. Power Frequency Withstand Voltage (Secondary/Primary) |  |  | kV | 28/3 |  | 70 / 3 |  |  |  |  | 33 kV | 1 | 170 / - | 70 / 3
11. Conductor Material (Primary / Secondary) |  |  |  | Cu/Cu |  | Cu/Cu
12. Temp. Rise | Windings |  | °C | 50 |  | 50 |  |  |  |  | 11 kV | 0 | 95 / - | 28 / 3
| Top Oil |  | °C | 45 |  | 55 |  |  |  |  | 7.2 kV | 0 | 75 / - | 28 / 3
13. Efficiency at 100% load (P.F = 0.8) |  |  | % |  |  | 98.5 |  |  |  |  | 7.2 kV | 0 | 60 / - | 20 / 3
14. Voltage regulation at 100% load (P.F = 0.8) |  |  | % |  |  | 3.96 |  |  |  |  | Custom Choise
15. No Load current |  |  | % |  |  | 0.51 |  | IEC Tolerances Applicable
16. Method of cooling |  |  |  | ONAN |  | ONAN
17. No load loss |  |  | W | 1200 |  | 695 |  | IEC Tolerances Applicable
18. Load loss |  |  | W | 10000 |  | 5394 |  | IEC Tolerances Applicable
19. Impedance voltage |  |  | % | 5% +- 10% |  | 5 |  | IEC Tolerances Applicable
20. Sound level |  |  | dB |  |  | 59
21. Dimensions
| Length |  | mm | 1260 |  | 1479 |  | Approximately
| Width |  | mm | 1000 |  | 1000 |  | Approximately
| Height |  | mm | 1210 |  | 1625 |  | Approximately
22.Total Weight |  |  | kg | 1310 |  | 1730 |  | Approximately
23.Oil Weight |  |  | kg | 250 |  | 395 |  | Approximately
24.Un-tanking Weight |  |  | kg |  |  |  |  | Approximately
25. Availabilty of Cable box in Primary side, Y/N | [5 empty] | N |  |  | Y
26. Availabilty of Cable box in Secondary side, Y/N | [5 empty] | N |  |  | N
27. Hermetically sealed/Conservator |  |  |  | Hermetically sealed |  | Hermetically sealed |  |  | Includes in ISD | Hermetically sealed |  | Galvanize & Powder |  |  | RAL6028 | Dark Green | C1
28. Painting Method, Galvanize/Marine paint/Powder |  |  |  | Shot Blast & Powder |  | Shot Blast & Powder |  | C3 |  | Conservator |  | Shot Blast & Marine paint |  |  | RAL9002 | White | C2
29. Unit Colour |  |  |  | RAL7033(C3M) |  | RAL7033 |  | Cement Grey |  |  |  | Shot Blast & Powder |  |  | RAL7032 | Pebble Grey | C3
30. Service conditions | [14 empty] | RAL7033 | Cement Grey | C4
| Max. ambient temp. |  | °C | 55 | [10 empty] | RAL7031 | Dark Admiralty Grey | C5-I
| Monthly average temp. |  | °C | [13 empty] | C5-M
| Yearly average temp. |  | °C
31. Altitude (Maximum) |  |  | m |  |  | 1000
32. Standard | [5 empty] | IEC60076:2011
33. Protection Available |  | 34. Changes by customer (if any)
ISD (includes protection for oil level, oil temp.,pressure & gas ) | Y
Oil Level Indicator | Includes in ISD |  | Designation |  | Sig. |  |  | Date
Pressure Release Device (Without Contacts) | Y | Designed by: | EE |  |  |  |  | 2023-06-19
Winding Temperature Indicator | N | Reviewed by: | EE |  |  |  |  | 2023-06-19
Bi- Directional Rollers | N | Approved by: | MDC |  |  |  |  | 2023-06-19
Revision No.: 00/25-05-2021
Note on H37: Eranga: =Q!B114
Note on H38: Eranga: =Q!B115
Note on H39: Eranga: =Q!B116
Note on H40: Eranga: =Q!B117
Note on H41: Eranga: =Q!B118
Note on H42: Eranga: =Q!B120

## DDOS
LTL TRANSFORMERS (PVT.) LTD. FRM/DE/01
DESIGN DATA OUTPUT SHEET
CORE DETAIL |  | B (T) : 1.750 | L (mm) : 52 |  |  | WT. (Kg) |  | L | #REF! | #REF!
V/T : 29.950 | GRADE : 27ZH00 | C - C (mm) : 656 | W1 / W2 / W3 / W4 (mm) : 39 / 36.5 / 27.5 / 18 (HV) + 36 (LV) |  |  |  |  | W1 | #REF! | #REF!
AREA : 770.9 cm2 |  | W - H (mm) : 890 | A (mm) : 294 | H (mm) : 300 |  | 704.6
|  |  |  | T1 / T2 / T3 / T4 (mm) : 290 / 260 / 220 / 180 |  | 1039.3 / 863.1 / 548.9 / 296.9
WINDING TYPE |  | LV |  |  | HV
VOLTS (L/PH) V |  | 415 / 239.6 |  |  | 33000 / 33000
CURRENT (L/PH) A |  | 5564.822 / 5564.822 |  |  | 69.982 / 40.404
CONNECTION |  | yn |  |  | D
TEST (PF / IMP.) kV |  | 3 / - |  |  | 70 / 170 |  |  |  | 70 / 200 | 33 kV
TURNS |  | 8 |  |  | 1157 / 1102 |  |  |  | 70 / 170 | 33 kV |  | L | 1102 | 5 | 12
LAYERS |  | 8 |  |  | 23 |  |  |  | 28 / 75 | 11 kV
TURNS / LAYER |  | 1 |  |  | 51.00/ 35.00 * |  |  |  | 20 / 60 | 7.2 kV
INSULATION |  | (0.25 + 0.25 SL x 838) DDP Between Layers |  |  | (0.15 + 0.25 SL x 838) DDP Between Layers |  |  |  | 3 / - | LV
(0.15 + 0.25 + 0.25 SL x 838) DDP Between Layers
1 & 2 , 13 & 14 , 14 & 15
EDGE STRIP (mm) |  | 18 x 0.25mm |  |  | (45 - 59.4) x 0.25mm
COOLING DUCT |  | Full Cooling Duct Between Layers 4 & 5 (838 x 1170 mm) |  |  | Full Cooling Duct Between Layers 5 & 6 (838 x 1480 mm)
|  | - |  |  | Full Cooling Duct Between Layers 11 & 12 (838 x 1750 mm)
|  | - |  |  | Full Cooling Duct Between Layers 17 & 18 (838 x 2010 mm)
COND. SIZE BARE (mm) |  | 800.00 x 3.00 |  |  | 6.700 x 2 |  |  | x 2
COND SIZE COVD. (mm) |  | 800.00 x 3.00 |  |  | 7.2 x 2
COND. AREA (mm2) |  | 2399.665 |  |  | 35.081
AMPS / mm2 |  | 2.319 |  |  | 1.152
LEAD SIZE (mm) |  | 100.000 / 20.000 |  |  | 7/1.7 bare copper |  | HD Copper - 3 mm dia paper covered
FLEXIBLE SIZE (mm) |  | 100.000 / 20.000 |  |  | 19/1.35 bare copper
RADIALS (mm) |  | 32.71/ 32.71/ 32.71 |  |  | 109.00/109.00/109.00 |  | 7/1.7 bare copper
I.D/O.D (mm) |  | 307 x 338 / 373 x 445 |  |  | 415 x 487 / 633 x 707 |  | 19/1.35 bare copper | [7 empty] | 307 | 414.421
ELEC./WDG. LGTH. (mm) |  | 800.00 / 840.000 |  |  | 735.600 / 840.000 | [9 empty] | 358.095 | 465.516
EQ. MEAN DIAM. (mm) |  | 186.1193 |  |  | 277.98 | [9 empty] | 372.421 | 632.421
MEAN TURN (m) |  | 1169.422 |  |  | 1746.6 | [9 empty] | 423.516 | 683.516
WEIGHT TOTAL (Kg) |  | 728.90 |  |  | 2032.86 | [9 empty] | 21
RESIST / PH (Ohm) |  | 8.2E-050 @ 75 C |  |  | 1.1500 @ 75 C
12R + DIR STRAY (W) |  | #VALUE! |  |  | #VALUE!
BUSHING |  | EN 3150 x 8 |  |  | Plug-in Type 36 kV 630 A Interface C x 3
CLEARANCES | CORE / LV : 3.50x 3.50x 10.00 mm |  | LV/HV : | 21.000 mm | HV/HV : 23.000 mm | YOKE/COVER/BASE : 280 / 41 mm
LV INNER TUBE | 2 mm PB + 4.5 mm CD (690 x 1100 mm) |  | STICK BARRIER : | 20 mm {2mm Type B CB + (6+6+4 PB) + 2mm Glue Allowance} x 690 mm x 1000 mm
[9 empty] | Total | Noinal | No. of tap pos | Deviation
TAP | TURNS | LOSSES | CALCULATED | GUARANTEED |  | WEIGHTS (Kg) |  |  | 1157 | 1102 | 5 | 27.5 | 1047 | 4 | 5
1 | 0 | CAPACITY (kVA) | 4000 | 4000 | LV CU | 603.53
2 | 1047 |  |  |  | HV CU | 1905.56
3 | 1075 | CU LOSS (W) | 10273 @ 75 C | 16805 | CU LEAD / BUSBAR | 184.33
4 | 1102 | FE LOSS (W) | #VALUE! | 2990 | TOTAL CU | 2693.42
5 | 1102 |  |  |  | CORE | 3500
6 | 1130 | TOTAL LOSS (W) | #VALUE! |  | LV INSULATION | 10.31
7 | 1157 | REACTANCE (%) | 7.688 |  | HV INSULATION | 67.95
8 |  | IMPEDANCE (%) | 7.692 | #VALUE! | CORE AND WDGS | 6310
9 |  | NO LOAD CURRENT (%) | 0.51 |  | OIL WEIGHT | 2828
10 |  | T. RISE OIL (°C) | #VALUE! | 55 | WEIGHT OF RADIATOR | 1205
11 |  | T. RISE WDG. (°C) | 60.5 | 50 | TOTAL WEIGHT | 12985 |  |  | 60.5 | 50.3
12 |  | X/R | 30 |  | EXPANSION OIL VOLUME | #VALUE!
TANK INSIDE | LENGTH (mm) : 2093 |  |  | WIDTH (mm) : | 936 | HEIGHT (mm) : 1811
[5 empty] | CORRUG. L.S DEPTH (mm) : | NO.:
HEIGHT OF RADIATOR : |  | 0 |  |  | CORRUG. S.S DEPTH (mm) : | NO.:
NUMBER OF RADIATORS : |  | 6 | CENTER LENGTH OF THE RADIATOR (mm) : |  | 1300
NUMBER OF ELEMENTS PER RADIATOR : |  | 6 | TYPE OF RADIATOR : |  |  |  | CENTERED
OFF CENTERED
RATING DETAILS
kVA | 4000 | VECTOR | Dyn11 | COOLING | ONAN | CONTINUOUS : Y
PHASE | 3 | Hz | 50 | VOLTAGE RATIO : 137.73 |  | TYPE OF UNIT : Hermetically sealed | Hermetically sealed
TAPPINGS ON HV |  | ABOVE NOMINAL : | 2 | IN STEPS OF : 2.5 %
|  | BELOW NOMINAL : | 2 | TAP CHANGER TYPE : HM 25.44.885 (30kV 63A 131mm 5 Pos)
SPECIAL ACCESSORIES: |  | ISD
STANDARD : IEC 60076:2011
CUSTOMER | : Uganda - LMB procurement |  |  | DESIGNED | : | DATE :
DESIGN NO | : 400033415 |  |  | Q.C.M. | : | DATE :
CONTRACT NO : | : |  |  | AUTHORIZED | : | DATE :
Revision:02/01-07-2009
ISD / HV Enclosure 36kV 250A Interface B Plug-in Type Bushings / LV DT3150 Cable Box (6 runs per phase & neutral)

## DDOSnew
LTL TRANSFORMERS (PVT.) LTD. FRM/DE/01
DESIGN DATA OUTPUT SHEET
GENERAL SPECIFICATIONS
kVA |  |  | 4000 |  | VECTOR | Dyn11
PHASE |  |  | 3 |  | Hz | 50
WINDING TYPE |  | LV |  |  | HV
CONDUCTOR MATERIAL |  | Al |  |  | Al
VOLTS (L/PH) V |  | 415 / 239.6 |  |  | 33000 / 33000
CURRENT (L/PH) A |  | 5564.822 / 5564.822 |  |  | 69.982 / 40.404
CONNECTION |  | yn |  |  | D
MAJOR PRODUCT DATA
LEAD SIZE (mm) |  | 100.000 / 20.000 |  |  | 7/1.7 bare copper
FLEXIBLE SIZE (mm) |  | 100.000 / 20.000 |  |  | 19/1.35 bare copper
BUSHING |  | EN 3150 x 8 |  |  | Plug-in Type 36 kV 630 A Interface C x 3
OIL WEIGHT (kg) |  | 2828
EXPANSION OIL VOLUME (L) |  | #VALUE!
TANK INSIDE | LENGTH(mm) | 2093
| WIDTH(mm) | 936
| HEIGHT(mm) | 1811
HEIGHT OF RADIATOR(mm) |  | 0
CORRUG. L.S DEPTH (mm)
CORRUG. S.S DEPTH (mm)
No. of RIBS |  | /
DATA FOR TESTING
RESIST / PH (Ohm) |  | 8.61E-50 @ 75 C |  |  | 1.2075 @ 75 C
T. RISE OIL (°C) | CALCULATED | #VALUE!
| GUARANTEED | 55
T. RISE WDG. (°C) | CALCULATED | 60.5
| GUARANTEED | 50
DATA FOR TAPPINGS
TAP CHANGER TYPE |  | HM 25.44.885 (30kV 63A 131mm 5 Pos)
IN STEPS OF |  | 2.5 %
ABOVE/ BELOW NOMINAL |  | 2 / 2
SPECIAL ACCESSORIES:
LIST |  | ISD, SAMB, LV Cable box
STANDARD : IEC 60076:2011
CUSTOMER | : Uganda - LMB procurement |  |  | DESIGNED | : | DATE : 23/8/2021
DESIGN NO | : 400033415 |  |  | REVIEWED | : | DATE : 23/8/2021
CONTRACT NO : | : |  |  | APPROVED | : | DATE : 23/8/2021
Revision:0/1/6/2021