## R
ta File Name: D:\LT | LTrafoDesign\ReportV | at
* Using Standard Da | ta from Files ***
TE: 2023.03.31 |  | IQUID TYPE TRANSFOR | MER CALCULATION (Ver | n 6.10.0) |  | Time: 13:58:54
DER : 30033415 | DESIGN: Data Set 1 | ENGINEER: LASINDU | CUSTOMER NAME | EYLAX
A - 300 Liquid | Type ONAN Cooli | 55 C Rise Th | ree Phase 50 Hz | Style Number:
: 33000 + 2- 2x 2. | 50 % TC: Off-load T | Changer | BIL: 170 (Delt | Line/Coil Amps: |  | 5.249/ 3.030
: 415 |  |  | BIL: 3 (Wye | Line/Coil Amps: |  | 417.362/ 417.362
------------------- | -------------------- | ----- S T A C K E D | C O R E -------- | --------- Width -- |  | Build ----- Weight -
Core Design.......: | OVAL Mitered | Diagonal Dimension: | 150.000 x 211.661 mm | Step 1: 150.000, |  | 59.834 mm 188.6 kg
Grade/Frame Type..: | 23ZDKH / 3-Leg | Window Height.....: | 377.000 mm | Step 2: 140.000, |  | 54.280 mm 159.7 kg
INDUCTION.........: | 1.750 Tesla | Center to Center..: | 317.365 mm | Step 3: 120.000, |  | 35.880 mm 90.5 kg
VPT, W/kg, PBase..: | 9.215, 1.011, 0.86 | Gross/Net CSA.....: | 245.3 / 237.2 cm2 | Step 4: 100.000, |  | 21.850 mm 45.9 kg
100 % Exc Current.: | 0.6049 | Weight of Core-Leg: | 275.8 kg | Step 5: 70.000, |  | 20.930 mm 30.8 kg
Sound/Natural Freq: | 51.5 db / 1200 Hz | Weight of Yoke....: | 217.4 kg | Step 6: 0.000, |  | 0.000 mm 0.0 kg
Peak HV Inrush Cur: | 65 amp | Core Net Weight...: | 493.2 kg | Step 7: 0.000, |  | 0.000 mm 0.0 kg
Utilization Factor: | 0.9206 | Core Scrap Weight.: | 22.3 kg | Step 8: 0.000, |  | 0.000 mm 0.0 kg
Standard Core No..: | NONE STANDARD | Core Gross Weight.: | 515.4 kg | Step 9: 0.000, |  | 0.000 mm 0.0 kg
Ovality Factor....: | 1.297 | Use Max Steel Wi | dth (Steps minus 1) | Using Std | S | teel Widths
Step Lead Allow...: | 3.917 mm | Main Step Lead Add: | 1.8 mm | Lead Allowance for |  | Last Step on LV Side
Core Perimeter....: | 594.6 mm | Delta Build.......: | 59.8 mm
Adjusted Widths...: | 150.00 / 140.00 / | .00 / 100.00 / 70. | 00
Adjusted Builds...: | 61.66 / 54.28 / | .88 / 21.85 / 17. | 01 (Delta Build 6 | 6)
------------------- | -------------------- | L O W V O L T A | G E W I N D I N G | ------------------ | - | --------------------
Type of Coil......: | CU-Foil | Coil-Length.......: | 350.000 mm | ELECT LENGTH...... | : | 330.000 mm
TURNS PER COIL....: | 1 x 26.0 | Inside Dimensions.: | 153.000 x214.661 mm | Strip-#x#x Wd x Tk | : | 1x1x 330.00 x 0.550
CURRENT DENSITY...: | 2.300 A/mm2 | Outside Dimensions: | 191.763 x262.424 mm | Cond/Lead Weight.. | : | 83.44 / 4.77 kg
|  | Inner Perimeter...: | 600.3 mm
Cooling Ducts Tk/#: | 4.500 mm / 0.67 | Rad Blds (H,Leg,L): | 23.88/ 19.38/ 23.88 | Lay/Trn/Duc Wts... | : | 3.89/ 0.00/ 0.27
Eff No Cool Ducts.: | HV: 1 Leg: 0 LV: 1 | Axial Allowance...: | 0.000 mm | Total Insul Weight | : | 4.16 kg
Short-Circuit Curr: | 20216 Amp. | Num Support Sticks: | 12
Mean Turn Length..: | 657.806 mm | Lead: Wd / Tk..: | 38.000 / 4.000 mm | Total Coil Weight. | : | 92.37 kg
Max Turn Lth Buckl: | 1912.336 mm | Bus Bar: Wd / Tk..: | 38.000 / 4.000 mm
|  | Layer Insul Tk....: | 0.180 mm
T-RISE/GRADIENT...: | 50.7/13.5 deg C | Watts/sq m .......: | 623.271 | Resistance (Coil). | : | 0.001975 @ 75 C
Turn CSA .........: | 181.500 mm2 |  |  | Conductor Dims.... | : | Specified Size
------------------- | -------------------- | I G H V O L T A | G E W I N D I N G | ------------------ | - | --------------------
Type of Coil......: | Layer-Wound Coil | Coil-Length.......: | 350.000 mm | Cond Mec/Elec Lgth | : | 284.000 / 282.767
Conductor.........: | CU-Round | Inside Dimensions.: | 227.763 x 298.424 | Cond-Dim Per Turn. | : | 1x1x 1.150 x 1.150
Turns Tot./Nominal: | 3760/ 3581 | Outside Dimensions: | 296.365 x 367.026 | Cond Area Per Turn | : | 1.03869 mm2
Cooling Ducts Tk/#: | 4.500 mm / 1.00 | Rad Blds (H,Leg,L): | 34.30/ 34.30/ 34.30 | HV Conductor Wt... | : | 99.38 kg
Eff No Cool Ducts.: | HV: 1 Leg: 1 LV: 1 | Add Rad Allowance.: | 0.000 mm | Lay/Trn/Duc Wts... | : | 15.84/ 0.00/ 0.58
Mean Turn Length..: | 946.6 mm | Layer/Turn Ins Bd.: | 0.850/ 0.083 mm | Insulation Weight. | : | 16.42 kg
LayIns Tk.........: | (15 Full) 0.850 mm | LayIns RB W/OvBld.: | 7.74 mm | Average LayIns Tk. | : | (Strip) 0.490 mm
CURRENT DENSITY...: | 2.917 A/mm2 | # Sup Pts/Ax All..: | 12 / 0.000 mm | Total Coil Weight. | : | 115.80 kg
# Lay: Max/Min tpl: | 17# 229.00/ 96.00 * | Axial Sections....: | 1 | Layer-Layer Volts. | : | 4226.8
T-RISE/GRADIENT...: | 54.6/17.4 deg C | Watts/sq m .......: | 666.426 | Resistance (Coil). | : | 68.4047 @ 75 C
|  |  |  | Conductor Dims.... | : | Standard Size
------------------- | -------------------- | L E C T R I C A L | C L E A R A N C E | ------------------ | - | --------------------
LV to Core Leg(mm): | 1.50x 1.50x 7.00 | LV Cond to Yoke...: | 23.500 mm | Total HV-LV Offset | : | 46.000 mm
Eff Hi-Lo ElecSpan: | 18.000 mm | Ph-Ph Elec Spacing: | 21.000 mm | Max LV Sup Span... | : | 47.000 mm
HV-HSide/HV-LSide.: | 50.00 / 50.00 mm | HV-Ends...........: | 50.000 mm | Yoke-Case Top/Bot. | : | 195.00 / 41.00 mm
HV Fixed Gap......: | 0.000 mm
-------- BASIS FOR | CALCULATIONS ------- | ------------------- | -- MATERIAL PRICES | USD/KG (17-08-01 | ) | -------------------
Netw.Short Cir.Cap: | 1500.0 MVA | E Rnd Wire: AL/CU.: | 4.56 / 11.73 | Core Cost......... | : | 3.88
Wdg Rise Limit....: | 55.0 deg C | Rect Wire : Al/Cu.: | 5.63 / 7.37 | Turn/Lay/DD Insul. | : | 2.18 / 3.28 / 4.1
Top Oil Rise Limit: | 50.0 deg C | Foil Cond: AL/CU..: | 3.59 / 11.73 | Mineral/Silicone.. | : | 0.98 / 6.12
Max No Load/Load..: | 550 / 3900 | LME/1000 (CU/AL)..: | 0 / 0 | Case Steel/Cooling | : | 0.78 / 1.71
------------------- | -------------------- | WEIGHTS, DIMENSIONS | , AND COOLING (RIBS) | ------------------ | - | --------------------
Active Part Weight: | 711 kg | Conservator Weight: | 7.12 kg | C&C Dim: Ht/Lgth.. | : | 677.00/ 931.10 mm
Clamp & Brace Wt..: | 71 kg | H-L Barrier Weight: | 9.55 kg
Mineral Oil Weight: | 320 kg | Ribs-Press/Weight.: | 0.20 kp/cm2 101 | Rib Height:1,2,3,4 | : | 700/ 700/ 700/ 700
Bus bar/TC Weight.: | 3/ 0 kg | Rib Pitch: 1,2,3,4: | 55/ 55/ 55/ 55 | No of Ribs:1,2,3,4 | : | 18/ 8/ 18/ 8
Cov/Case & Cooling: | 23/ 142 kg | Rib Depth: 1,2,3,4: | 120/ 120/ 120/ 120 | Rib Pan Wd:1,2,3,4 | : | 1031/ 483/1031/ 483
Total Weight......: | 1270 kg | Rib Thick: 1,2,3,4: | 1.20/1.20/1.20/1.20 | Case: Lt/Wd/Ht(mm) | : | 1031.1x 483.3x 913.0
------------------- | -------------------- | ------PRICE & COST | IN USD UNITS ------- | ------------------ | - | --------------------
Core Cost.........: | 1913 | HV / LV Coil Cost.: | 1271/ 1052 | Labor & VOH/Hours. | : | 0 / 0
Case/Cooling Cost.: | 32/ 173 | Bracing Cost......: | 55 | Design Matl-Cost.. | : | 5088
Mineral Oil.......: | 313 | Assy and Misc.....: | 278 | Variable Cost..... | : | 5088
EVALUATED LOSSES..: | 8994 | EVALUATED COST....: | 14083 | RECOMMENDED PRICE. | : | 10177
------------------- | -------------------- | ---------- PERFORMA | NCE DATA ----------- | ------------------ | - | --------------------
HV Wdg DC Losses..: | 1884 Watts | LV Wdg DC Losses..: | 1032 Watts
HV Watts (% Eddy).: | 1889 ( 0.3) | LV Watts (% Eddy).: | 1082 ( 3.1) | LV Bus Bar / Stray | : | 45 / 75
No Load Losses....: | 499 Watts | Tot-Ld Watts(%Ed).: | 3091 ( 5.1) | Total Losses(ONAN) | : | 3590 @ 75 C
% X / % R / % Lead: | 4.02/1.03/0.02 % | % Z (HV-LV-Lead)..: | 4.164 % | TOP OIL RISE...... | : | 46.5 deg C
|  | % Z Guaranteed....: | 4.000 %
------------------- | -------------------- | ------------------- | -------------------- | ------------------ | - | --------------------
TES: HV Axial & Ra | d Factors - 1.000, | 950 LV Rad Fact | or - 0.970 OPT | : (Min Evaluated C | o | st )
MARG/MULT.: < | Rise>: Top Oil= 0 H | 0 L= 0 T= 0 <Loss | >: Core= 1.000 BusB= | 1.0 Eddy H= 1.0 | L | = 1.0 Stray= 1.0
CORE: Std(NO | ) Wds(YES) C-C(NO ) | g(NO ), COND: Foil | Tk(NO ), CLEAR: Wd | O ), CASE: Std(NO |  | ) CALC: Sh Cir(YES)
Circuit Load | Factors: HV= 1.000, | LV= 1.000, TV= 1. | 000
Circuit Load | Factors: HV= 1.000, | LV= 1.000, TV= 1. | 000
Using LTL Cor | e Loss Calculation T | nical Standard: < N | O >
Using LTL Loa | d Loss Calculation T | nical Standard: < N | O >
Impedance Mod | el: Convensional
Tapping Turns | @.......: 1 - 3760, | - 3670, 3 - 3581, 4 | - 3491, 5 - 3402

## P
| Section | Value | Row No | Column No
| Start | DESIGN: Data Set 1 | 7 | 2
| Core | C O R E -------- | 10 | 4
| LV | L O W V O L T A | 24 | 3
| HV | I G H V O L T A | 36 | 3
| Clearances | L E C T R I C A L | 47 | 3
| Calculations | CALCULATIONS ------- | 51 | 2
| Weights & Dimensions | WEIGHTS, DIMENSIONS | 18 | 3
| Prices | IN USD UNITS ------- | 61 | 4
| Performance data | NCE DATA ----------- | 65 | 4
| Factors | -------------------- | 70 | 4
Start | 0 | 1 | 2 | 3 | 4 | 5 | 6
-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-1 | TE: 2023.03.31 | 0 | IQUID TYPE TRANSFOR | MER CALCULATION (Ver | n 6.10.0) | 0 | Time: 13:58:54
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | DER : 30033415 | DESIGN: Data Set 1 | ENGINEER: LASINDU | CUSTOMER NAME | EYLAX | 0 | 0
2 | A - 300 Liquid | Type ONAN Cooli | 55 C Rise Th | ree Phase 50 Hz | Style Number: | 0 | 0
3 | : 33000 + 2- 2x 2. | 50 % TC: Off-load T | Changer | BIL: 170 (Delt | Line/Coil Amps: | 0 | 5.249/ 3.030
4 | : 415 | 0 | 0 | BIL: 3 (Wye | Line/Coil Amps: | 0 | 417.362/ 417.362
5 | ------------------- | -------------------- | ----- S T A C K E D | C O R E -------- | --------- Width -- | 0 | Build ----- Weight -
6 | Core Design.......: | OVAL Mitered | Diagonal Dimension: | 150.000 x 211.661 mm | Step 1: 150.000, | 0 | 59.834 mm 188.6 kg
Core
0 | ------------------- | -------------------- | ----- S T A C K E D | C O R E -------- | --------- Width -- | 0 | Build ----- Weight -
1 | Core Design.......: | OVAL Mitered | Diagonal Dimension: | 150.000 x 211.661 mm | Step 1: 150.000, | 0 | 59.834 mm 188.6 kg
2 | Grade/Frame Type..: | 23ZDKH / 3-Leg | Window Height.....: | 377.000 mm | Step 2: 140.000, | 0 | 54.280 mm 159.7 kg
3 | INDUCTION.........: | 1.750 Tesla | Center to Center..: | 317.365 mm | Step 3: 120.000, | 0 | 35.880 mm 90.5 kg
4 | VPT, W/kg, PBase..: | 9.215, 1.011, 0.86 | Gross/Net CSA.....: | 245.3 / 237.2 cm2 | Step 4: 100.000, | 0 | 21.850 mm 45.9 kg
5 | 100 % Exc Current.: | 0.6049 | Weight of Core-Leg: | 275.8 kg | Step 5: 70.000, | 0 | 20.930 mm 30.8 kg
6 | Sound/Natural Freq: | 51.5 db / 1200 Hz | Weight of Yoke....: | 217.4 kg | Step 6: 0.000, | 0 | 0.000 mm 0.0 kg
7 | Peak HV Inrush Cur: | 65 amp | Core Net Weight...: | 493.2 kg | Step 7: 0.000, | 0 | 0.000 mm 0.0 kg
8 | Utilization Factor: | 0.9206 | Core Scrap Weight.: | 22.3 kg | Step 8: 0.000, | 0 | 0.000 mm 0.0 kg
9 | Standard Core No..: | NONE STANDARD | Core Gross Weight.: | 515.4 kg | Step 9: 0.000, | 0 | 0.000 mm 0.0 kg
10 | Ovality Factor....: | 1.297 | Use Max Steel Wi | dth (Steps minus 1) | Using Std | S | teel Widths
11 | Step Lead Allow...: | 3.917 mm | Main Step Lead Add: | 1.8 mm | Lead Allowance for | 0 | Last Step on LV Side
12 | Core Perimeter....: | 594.6 mm | Delta Build.......: | 59.8 mm | 0 | 0 | 0
13 | Adjusted Widths...: | 150.00 / 140.00 / | .00 / 100.00 / 70. | 00 | 0 | 0 | 0
14 | Adjusted Builds...: | 61.66 / 54.28 / | .88 / 21.85 / 17. | 01 (Delta Build 6 | 6) | 0 | 0
LV
1 | ------------------- | -------------------- | L O W V O L T A | G E W I N D I N G | ------------------ | - | --------------------
2 | Type of Coil......: | CU-Foil | Coil-Length.......: | 350.000 mm | ELECT LENGTH...... | : | 330.000 mm
3 | TURNS PER COIL....: | 1 x 26.0 | Inside Dimensions.: | 153.000 x214.661 mm | Strip-#x#x Wd x Tk | : | 1x1x 330.00 x 0.550
4 | CURRENT DENSITY...: | 2.300 A/mm2 | Outside Dimensions: | 191.763 x262.424 mm | Cond/Lead Weight.. | : | 83.44 / 4.77 kg
5 | 0 | 0 | Inner Perimeter...: | 600.3 mm | 0 | 0 | 0
6 | Cooling Ducts Tk/#: | 4.500 mm / 0.67 | Rad Blds (H,Leg,L): | 23.88/ 19.38/ 23.88 | Lay/Trn/Duc Wts... | : | 3.89/ 0.00/ 0.27
7 | Eff No Cool Ducts.: | HV: 1 Leg: 0 LV: 1 | Axial Allowance...: | 0.000 mm | Total Insul Weight | : | 4.16 kg
8 | Short-Circuit Curr: | 20216 Amp. | Num Support Sticks: | 12 | 0 | 0 | 0
9 | Mean Turn Length..: | 657.806 mm | Lead: Wd / Tk..: | 38.000 / 4.000 mm | Total Coil Weight. | : | 92.37 kg
10 | Max Turn Lth Buckl: | 1912.336 mm | Bus Bar: Wd / Tk..: | 38.000 / 4.000 mm | 0 | 0 | 0
11 | 0 | 0 | Layer Insul Tk....: | 0.180 mm | 0 | 0 | 0
12 | T-RISE/GRADIENT...: | 50.7/13.5 deg C | Watts/sq m .......: | 623.271 | Resistance (Coil). | : | 0.001975 @ 75 C
13 | Turn CSA .........: | 181.500 mm2 | 0 | 0 | Conductor Dims.... | : | Specified Size
HV
2 | ------------------- | -------------------- | I G H V O L T A | G E W I N D I N G | ------------------ | - | --------------------
3 | Type of Coil......: | Layer-Wound Coil | Coil-Length.......: | 350.000 mm | Cond Mec/Elec Lgth | : | 284.000 / 282.767
4 | Conductor.........: | CU-Round | Inside Dimensions.: | 227.763 x 298.424 | Cond-Dim Per Turn. | : | 1x1x 1.150 x 1.150
5 | Turns Tot./Nominal: | 3760/ 3581 | Outside Dimensions: | 296.365 x 367.026 | Cond Area Per Turn | : | 1.03869 mm2
6 | Cooling Ducts Tk/#: | 4.500 mm / 1.00 | Rad Blds (H,Leg,L): | 34.30/ 34.30/ 34.30 | HV Conductor Wt... | : | 99.38 kg
7 | Eff No Cool Ducts.: | HV: 1 Leg: 1 LV: 1 | Add Rad Allowance.: | 0.000 mm | Lay/Trn/Duc Wts... | : | 15.84/ 0.00/ 0.58
8 | Mean Turn Length..: | 946.6 mm | Layer/Turn Ins Bd.: | 0.850/ 0.083 mm | Insulation Weight. | : | 16.42 kg
9 | LayIns Tk.........: | (15 Full) 0.850 mm | LayIns RB W/OvBld.: | 7.74 mm | Average LayIns Tk. | : | (Strip) 0.490 mm
10 | CURRENT DENSITY...: | 2.917 A/mm2 | # Sup Pts/Ax All..: | 12 / 0.000 mm | Total Coil Weight. | : | 115.80 kg
11 | # Lay: Max/Min tpl: | 17# 229.00/ 96.00 * | Axial Sections....: | 1 | Layer-Layer Volts. | : | 4226.8
12 | T-RISE/GRADIENT...: | 54.6/17.4 deg C | Watts/sq m .......: | 666.426 | Resistance (Coil). | : | 68.4047 @ 75 C
13 | 0 | 0 | 0 | 0 | Conductor Dims.... | : | Standard Size
14 | ------------------- | -------------------- | L E C T R I C A L | C L E A R A N C E | ------------------ | - | --------------------
Clearances
3 | ------------------- | -------------------- | L E C T R I C A L | C L E A R A N C E | ------------------ | - | --------------------
4 | LV to Core Leg(mm): | 1.50x 1.50x 7.00 | LV Cond to Yoke...: | 23.500 mm | Total HV-LV Offset | : | 46.000 mm
5 | Eff Hi-Lo ElecSpan: | 18.000 mm | Ph-Ph Elec Spacing: | 21.000 mm | Max LV Sup Span... | : | 47.000 mm
6 | HV-HSide/HV-LSide.: | 50.00 / 50.00 mm | HV-Ends...........: | 50.000 mm | Yoke-Case Top/Bot. | : | 195.00 / 41.00 mm
7 | HV Fixed Gap......: | 0.000 mm | 0 | 0 | 0 | 0 | 0
8 | -------- BASIS FOR | CALCULATIONS ------- | ------------------- | -- MATERIAL PRICES | USD/KG (17-08-01 | ) | -------------------
9 | Netw.Short Cir.Cap: | 1500.0 MVA | E Rnd Wire: AL/CU.: | 4.56 / 11.73 | Core Cost......... | : | 3.88
10 | Wdg Rise Limit....: | 55.0 deg C | Rect Wire : Al/Cu.: | 5.63 / 7.37 | Turn/Lay/DD Insul. | : | 2.18 / 3.28 / 4.1
Calculations
4 | -------- BASIS FOR | CALCULATIONS ------- | ------------------- | -- MATERIAL PRICES | USD/KG (17-08-01 | ) | -------------------
5 | Netw.Short Cir.Cap: | 1500.0 MVA | E Rnd Wire: AL/CU.: | 4.56 / 11.73 | Core Cost......... | : | 3.88
6 | Wdg Rise Limit....: | 55.0 deg C | Rect Wire : Al/Cu.: | 5.63 / 7.37 | Turn/Lay/DD Insul. | : | 2.18 / 3.28 / 4.1
7 | Top Oil Rise Limit: | 50.0 deg C | Foil Cond: AL/CU..: | 3.59 / 11.73 | Mineral/Silicone.. | : | 0.98 / 6.12
8 | Max No Load/Load..: | 550 / 3900 | LME/1000 (CU/AL)..: | 0 / 0 | Case Steel/Cooling | : | 0.78 / 1.71
9 | ------------------- | -------------------- | WEIGHTS, DIMENSIONS | , AND COOLING (RIBS) | ------------------ | - | --------------------
10 | Active Part Weight: | 711 kg | Conservator Weight: | 7.12 kg | C&C Dim: Ht/Lgth.. | : | 677.00/ 931.10 mm
11 | Clamp & Brace Wt..: | 71 kg | H-L Barrier Weight: | 9.55 kg | 0 | 0 | 0
Weights & Dimensions
-1 | ------------------- | -------------------- | WEIGHTS, DIMENSIONS | , AND COOLING (RIBS) | ------------------ | - | --------------------
0 | Active Part Weight: | 711 kg | Conservator Weight: | 7.12 kg | C&C Dim: Ht/Lgth.. | : | 677.00/ 931.10 mm
1 | Clamp & Brace Wt..: | 71 kg | H-L Barrier Weight: | 9.55 kg | 0 | 0 | 0
2 | Mineral Oil Weight: | 320 kg | Ribs-Press/Weight.: | 0.20 kp/cm2 101 | Rib Height:1,2,3,4 | : | 700/ 700/ 700/ 700
3 | Bus bar/TC Weight.: | 3/ 0 kg | Rib Pitch: 1,2,3,4: | 55/ 55/ 55/ 55 | No of Ribs:1,2,3,4 | : | 18/ 8/ 18/ 8
4 | Cov/Case & Cooling: | 23/ 142 kg | Rib Depth: 1,2,3,4: | 120/ 120/ 120/ 120 | Rib Pan Wd:1,2,3,4 | : | 1031/ 483/1031/ 483
5 | Total Weight......: | 1270 kg | Rib Thick: 1,2,3,4: | 1.20/1.20/1.20/1.20 | Case: Lt/Wd/Ht(mm) | : | 1031.1x 483.3x 913.0
6 | ------------------- | -------------------- | ------PRICE & COST | IN USD UNITS ------- | ------------------ | - | --------------------
7 | Core Cost.........: | 1913 | HV / LV Coil Cost.: | 1271/ 1052 | Labor & VOH/Hours. | : | 0 / 0
8 | Case/Cooling Cost.: | 32/ 173 | Bracing Cost......: | 55 | Design Matl-Cost.. | : | 5088
Prices
6 | ------------------- | -------------------- | ------PRICE & COST | IN USD UNITS ------- | ------------------ | - | --------------------
7 | Core Cost.........: | 1913 | HV / LV Coil Cost.: | 1271/ 1052 | Labor & VOH/Hours. | : | 0 / 0
8 | Case/Cooling Cost.: | 32/ 173 | Bracing Cost......: | 55 | Design Matl-Cost.. | : | 5088
9 | Mineral Oil.......: | 313 | Assy and Misc.....: | 278 | Variable Cost..... | : | 5088
10 | EVALUATED LOSSES..: | 8994 | EVALUATED COST....: | 14083 | RECOMMENDED PRICE. | : | 10177
11 | ------------------- | -------------------- | ---------- PERFORMA | NCE DATA ----------- | ------------------ | - | --------------------
12 | HV Wdg DC Losses..: | 1884 Watts | LV Wdg DC Losses..: | 1032 Watts | 0 | 0 | 0
13 | HV Watts (% Eddy).: | 1889 ( 0.3) | LV Watts (% Eddy).: | 1082 ( 3.1) | LV Bus Bar / Stray | : | 45 / 75
Performance data
7 | ------------------- | -------------------- | ---------- PERFORMA | NCE DATA ----------- | ------------------ | - | --------------------
8 | HV Wdg DC Losses..: | 1884 Watts | LV Wdg DC Losses..: | 1032 Watts | 0 | 0 | 0
9 | HV Watts (% Eddy).: | 1889 ( 0.3) | LV Watts (% Eddy).: | 1082 ( 3.1) | LV Bus Bar / Stray | : | 45 / 75
10 | No Load Losses....: | 499 Watts | Tot-Ld Watts(%Ed).: | 3091 ( 5.1) | Total Losses(ONAN) | : | 3590 @ 75 C
11 | % X / % R / % Lead: | 4.02/1.03/0.02 % | % Z (HV-LV-Lead)..: | 4.164 % | TOP OIL RISE...... | : | 46.5 deg C
12 | 0 | 0 | % Z Guaranteed....: | 4.000 % | 0 | 0 | 0
13 | ------------------- | -------------------- | ------------------- | -------------------- | ------------------ | - | --------------------
Factors
8 | ------------------- | -------------------- | ------------------- | -------------------- | ------------------ | - | --------------------
9 | TES: HV Axial & Ra | d Factors - 1.000, | 950 LV Rad Fact | or - 0.970 OPT | : (Min Evaluated C | o | st )
10 | MARG/MULT.: < | Rise>: Top Oil= 0 H | 0 L= 0 T= 0 <Loss | >: Core= 1.000 BusB= | 1.0 Eddy H= 1.0 | L | = 1.0 Stray= 1.0
11 | CORE: Std(NO | ) Wds(YES) C-C(NO ) | g(NO ), COND: Foil | Tk(NO ), CLEAR: Wd | O ), CASE: Std(NO | 0 | ) CALC: Sh Cir(YES)
12 | Circuit Load | Factors: HV= 1.000, | LV= 1.000, TV= 1. | 000 | 0 | 0 | 0
13 | Circuit Load | Factors: HV= 1.000, | LV= 1.000, TV= 1. | 000 | 0 | 0 | 0
14 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | Using LTL Cor | e Loss Calculation T | nical Standard: < N | O > | 0 | 0 | 0
16 | Using LTL Loa | d Loss Calculation T | nical Standard: < N | O > | 0 | 0 | 0
17 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Q
MARGINS
Core Loss | 10
Cu Loss | 10
No Load Current | 30
Total Weight | 100
Material Name in MM | Margin (%)
Fin Radiators | 0 | 0 |  | 2.5
| 0 | 0 |  | 2.5
Panel Type Radiators | 0 | 0 |  | 2.5 |  |  | Removable
Cover+Base+Flange | 0 | 0 |  | 2.5
Steel (Total) | 0 | 0 |  | 2.5
Wooden Total | 0 | 0 |  | 2.5
Core steel | 0 | 0 |  | 2.5
Oil | 0 | 0 |  | 2.5
Copper Foil | 0 | 0 |  | 2.5
Round Copper | 0 | 0 |  | 2.5
Copper Bus Bar | 0 | 0 |  | 2.5
Rectangular Copper | 0 | 0 |  | 2.5
DDP-Double Layer | 0 | 0 |  | 2.5
0.15 DDP-Single Layer | 0 | 0 |  | 2.5
0.25 DDP-Single Layer | 0 | 0 |  | 2.5
Strip Insulation | 0 | 0 |  | 2.5
Corrugator Boards- 9.0x2.0 mm | 0 | 0 |  | 2.5
LV Strip | 0 | 0 |  | 2.5
HV Strip | 0 | 0 |  | 2.5
Galvanizing | 0 | 0 |  | 2.5
Primer Paint & Thinner | 0 | 0 |  | 2.5
Powder Paint | 0 | 0 |  | 2.5
Rectangular Copper
ELECTRICAL DATA
TYPE | Fin Radiator |  |  | Ribs | Ribs-Press/Weight.:
| Conservator Type |  |  | Conservator | Conservator Weight:
| N | N
Hermetically Sealed
Conservator Type
Fin Radiator
Panel type
Y
N
kVA | 300 | 3 | 13 |  |  |  |  | Tap Wire | Area | Ph density | Line Density | ph (kg) | line (kg)
HV VOLTS | 33000 | 1 | 9 | 18 |  |  |  | 3 | 7.0686 | 0.42866 | 0.74258 | 4 | 1.3333
LV VOLTS | 415 | 1 | 7 |  |  |  |  | 7/1.7 | 15.8886 | 0.1907 | 0.33036 | 0 | 0
LV Coil current | 417.362 | 8 | 16 | 417.362/ 417.362 |  | 1 | 2 | 19/1.35 | 27.1964 | 0.11141 | 0.193 | 0 | 0
LV line current | 417.362 | [6 empty] | Choise |  | 0.42866 | 0.74258
LV Coil current density | 2.3 | 7
: 33000 + 2- 2x 2. | [7 empty] | Capacity | Tapping | Barrier DDP
HV coil current | 3.03 | 12 | 7 | 5.249/ 3.030 |  | Closest capacity | 300 | 100 | 3 | 0.5
HV line current | 5.249 |  |  |  |  | Tapping Weight | #N/A | 160 | 3 | 0.5
[8 empty] | 250 | 4 | 0.75
HV voltage (kV) | 33 | [6 empty] | 400 | 4 | 1
Basic Insulation Level | 170 | 4 | 10 |  |  |  |  | 630 | 5 | 1.5
%X | 4.02 | 16 | 10 | 5 | 4.02/1.03/0.02 % | % X / % R / % Lead: |  | 800 | 5 | 2
%R | 1.03 | [6 empty] | 1000 | 6 | 2.5
Frequency | 50 | 5 | 18 |  |  |  |  | 1250 | 6 | 3.5
Phases | 3 | ree | [5 empty] | 1600 | 7 | 4.5
Tappings |  | 9 | 12 | 18 |  |  |  | 2000 | 7 | 5.5
+ | 2 | [6 empty] | 2500 | 8 | 6.5
- | -2 | 2 | [5 empty] | 3150 | 13 | 7.5
Steps | 2.5 | 4 | 5
| 5% | 2 | 1
| 2.5% | 1 | 2
| 0% | 0 | 3
| -2.5% | -1 | 4
| -5% | -2 | 5
| - | 0
| - | 0
| - | 0
| - | 0
Vector Group
LV | yn |  | yn
HV | D |  | D
Dyn
Dyn11
Temp. Rise Windings | 55 | 11 | 55
Temp. Rise Top oil | 50 | 10 | 50
% impedence | 4.67 | 4.164 % | % Z (HV-LV-Lead)..: |  | 4.164 | 4.164
Full Load Loss | 3900 | 1.1 | 1082 |  |  | 3900
No Load Loss | 550 | 1.1 | #VALUE! | #VALUE! |  | 550 |  |  | 4.1484 | 0.36067
No load Current | 0.6049
Sound level | 52
Core Loss Factor | 1 | 16 | 8
Factor k x sqrt(2) | #VALUE! | #VALUE! | #VALUE!
kVA | % Z | % Z-pu | FL loss | NL loss | PU load | PF | X | sin X | %X | %R | %FE | %Eff | %Reg
300 | 4.67 | 4.67 | 3900 | 550 | 1 | 0.8 | 0.6435 | 0.6 | 4.4854 | 1.3 | 0.18333 | 98.1796 | 3.7707
DIMENSIONS
CASE
Case-Length | 1031 | 14 | 7 | 20
Case-Width | 483
Case-Height | 913
HEIGHTS |  | WEIGHTS
Conservator | 340 | 13
HV Box | 608 | 57
ISD | 0 | 0
Plug-in Type 36 kV 250 A Interface B | 150 | 15
EN 630 | 165 | 4.64
LV Box | 0 | 0
Height for base skid and cover | 90 | 22.6132
CABLE BOX
No of intakes /Phase (LV) | 4
LV Box Depth | 0 |  |  | Conservator Length | 185
LV Box Width | 0 |  |  | Panel Add. to Length | 0
HV Box Depth | 862 |  |  | Panel Add. to Width | 0
HV Box Width | 578
WTI Box Depth | 0
Tolerance
Length | 1236 | 20 | 1216
Width | 1365 | 20 | 1345
Height | 1631 | 20 | 1611
Weight-TOTAL | 1440 | 50 | 1382
Weight-OIL | 320 |  | 320
Weight-ACTIVE PART | 720 |  | 711
Weight-Untanking | 790 | 50 | 731
Container Arrangement |  | 40' |  |  | 20'
Length |  | 12045 |  |  | 5919
Width |  | 2280 |  |  | 2286
Weight | 100 | 27396 |  |  | 22100
Length/Length |  | 9 | 1 |  | 4 | 1
Length/Width |  | 8 | 1 |  | 4 | 1
Weight | 9 | 17 |  | 4 | 14
DESIGN
Design | 30033415 |  |  | DER : 30033415
Date | 2023.03.31 | 5 | 6 | Time: 13:58:54 | IQUID TYPE TRANSFOR |  |  | TE: 2023.03.31
Time | 13:58:54 | [6 empty] | 3
Customer | EYLAX
WINDING DATA
Coil Length | 350 | 348 | 284 | 282.767 | 330 | 0 | 1
Window height | 377 | 377.000 | 9
Center to center | 318 | 317.365 | 9
Core Type | OVAL
Height from yoke to cover | 195 | 41.00 mm | 41
LV layer insulations thickness | 0.18
INSULATION
LV layer insulations thickness | 0.15 | 0.18 | 3.89 | 38.000 | 0.180
348mm x 0.15 DDP DL | 3.89 | 1 |  |  |  | 0.15 DDP | 0.25 DDP | 0.15 DDP | 0.25 DDP
348mm x 0.15 DDP SL | 0 | 0 |  |  | 0.15 | 1 |  | 1
348mm x 0.25 DDP SL | 0 | 0 |  |  | 0.18 | 1 |  | 1
[5 empty] | 0.25 | 1 |  | 1
[5 empty] | 0.3 | 1 |  | 2
HV layer insulations thickness | 0.85 | 0.85 | 15.84 |  | 0.35 |  | 1 |  | 1
348mm x 0.15 DDP SL | 0 | 0 |  | 0.85 | 0.4 | 0.5 | 0.5 | 1 | 1
348mm x 0.25 DDP SL | 0.75 | 0 |  | 0.49 | 0.45 | 1 |  | 3
[5 empty] | 0.5 |  | 1 |  | 2
HV strip insulations thickness |  |  | 15.84 |  | 0.55 | 0.67 | 0.33 | 2 | 1
33 x 0.05 mm Strip | 18.9912 | 1 |  |  | 0.6 | 1 |  | 4
33 x 0.075 mm Strip | 0 | 0 |  |  | 0.65 |  | 1 |  | 2
[5 empty] | 0.7 | 0.75 | 0.25 | 3 | 1
348mm x 0.15 DDP DL | 3.89 |  |  |  | 0.75 |  | 1 |  | 3
348mm x 0.15 DDP SL | 0 |  |  |  | 0.8 | 0.5 | 0.5 | 2 | 2
348mm x 0.25 DDP SL | 0.75 |  |  |  | 0.85 | 0.8 | 0.2 | 4 | 1 | Edge Strips
[5 empty] | 0.9 | 0.25 | 0.75 | 1 | 3 | 8
LV edge strip | 8 |  |  |  | 0.95 |  | 1 |  | 3 | 18
20 | 0.5 | 13 | 19 |  | 1.00 |  | 1 |  | 4 | 27
657.806 | 26.0 | 3 | 10 | 3 | 1.1 | 0.66667 | 0.33333 | 4 | 2 | 33
| #VALUE! |  |  |  | 1.2 | 1 |  | 8 | 0 | 45
17102.956 | 0.44126 |  |  |  | 1.25 |  | 1 | 0 | 4
8 | 0.25 |  |  |  | 1.3 | 0.67 | 0.33 | 4 | 2
HV edge strip | 33 |  |  |  | 1.4 | 0.75 | 0.25 | 6 | 2
66 | 1.150 | 12 | 18 |  | 1.5 |  | 1 |  | 6
946.6 | 17 |  |  |  | 1.6 | 0.5 | 0.5 | 4 | 4
16092.2 | 3.1512 |  |  |  | 1.7 | 0.8 | 0.2 | 8 | 2
33 | 0.25 |  |  |  | 1.8 | 0.25 | 0.75 | 2 | 6
Duct Space |  |  |  |  | 1.9 |  | 1 |  | 6
LV | 0.27 | 18 | 12 | 5 | 2 |  | 1 |  | 8
HV | 0.58 | 19 | 13 | 6 | 2.1 | 0.4 | 0.6 |  | 8
| 0.85 |  |  |  | 2.2 | 0.66667 | 0.33333 | 1 | 8
Corragated Board |  |  |  |  | 2.3 | 0.17 | 0.83 | 2 | 10
| 9.55 | 6 |  |  | 2.45 | 0.23 | 0.77 | 3 | 10
CORE STEEL
Core Steel | Builds(mm) | Weight(kg) | : | . | "(10)" | "m" | *100 | "k" | Weight | Adjusted Build
150 | 60 | 188.6 | 7 | 13 | 60 | 8 | 0 | 19 | 188.6 | 62 |  | 150
140 | 55 | 159.7 | 7 | 13 | 55 | 8 | 0 | 19 | 159.7 | 55 |  | 140 | 17 | 1
120 | 36 | 90.5 | 7 | 13 | 36 | 8 | 0 | 19 | 90.5 | 36 |  | 120 | 17
100 | 22 | 45.9 | 7 | 13 | 22 | 8 | 0 | 19 | 45.9 | 22 |  | 100 | 6.5
70 | 21 | 30.8 | 7 | 13 | 21 | 8 | 0 | 19 | 30.8 | 6.5 |  | 70
0 | 0 | 0 | 7 | 13 | 0 | 7 | 0 | 18 | 0.0 | 0 |  |  | 70
0 | 0 | 0 | 7 | 13 | 0 | 7 | 0 | 18 | 0.0 | 0
0 | 0 | 0 | 7 | 13 | 0 | 7 | 0 | 18 | 0.0 | 0
0 | 0 | 0 | 7 | 13 | 0 | 7 | 0 | 18 | 0.0 | 0
TOTAL | 194 | 515.4 | 515.4
core steel type | 23ZDKH
core steel thickness | 23ZDKH85
COPPER
LV | CU-foil
AL-foil
CU-layer-rect
HV | CU-round
CU-rectangular
LV Cu
CU-Foil | 330.00 x 0.55 | 19 | 4 | 2
CU-Foil | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| 330.00 x 0.55 | 330 | 0.55
330.00 x 0.55mm CU-Foil | 83.44 | 83.44
HV Cu
CU-Round | 1.150 x 1.150 | 18 | 12 | 4 | 2 | 1
1.150
1.150mm CU-Round | 99.38 | 99.38
Flat Cu
LV Leads | 4.77 | 7 | 16
Bus Bars | 3
Total | 7.77 |  | 4 | 38 | 17 | 8 | 18
4*38mm | 5.7436
Inhibited Mineral Oil | 367.8161
STEEL
Steel Density (kg/mm3) | 7.85e-06
Steel Weights | From Program | Calculated
Cover | 23 | 20.3068 | 3 | 11
Case + Cooling | 142
Case | 41 | 47.4552
Clamps | 71 | 32.3492 | 4
Conservator | 7.12 | 33.912 | 6
| 142 | 134
142
Radiator Weights
Fin Type Radiators | 101 | 15 | 10
Panel Type Radiators | 0 | 6
101
101
Galvanize | 172.12
Steel Channel
MS Ch 76x38x6 , L= 1021mm | 840
MS Ch 100x50x6 , L= 1021mm | 1128
MS Ch 127x64x6 , L= 1021mm | 1458
MS Ch 152x76x6 , L= 1021mm | 1752
MS Ch 200x75x9 , L= 1021mm | 2988
4mm MS Plate 1021x217x4mm | 868
Base Skid
50x50x6 AI | 50 | 564
76x38x6 MS Channel | 76 | 840 |  | 400 upto including
100x50x6 MS Channel | 100 | 1128 |  | 1000 upto inc
152x152x10 H Iron | 152 | 4360 |  | 2500
250x75x9 MS Channel | 200 | 2988 |  | >2500
| Dimensions |  |  | MS Plate Arrangement-I |  |  | MS Plate Arrangement-II |  |  |  |  | WEIGHT
MS Sheet -Length | 2440
MS Sheet -Width | 1220
| Thickness | Width | Length | L/L | W/W | Nos | L/W | W/L | Nos | Nos of transformer | Required Nos
Cover plate | 4 | 543 | 1191 | 2 | 2 | 4 | 4 | 1 | 4 | 4 | 1 | 20.3068
Base | 3 | 1131 | 849 | 2 | 1 | 2 | 2 | 1 | 2 | 2 | 1 | 22.6132
Conservator | 3 | 1200 | 1200 | 2 | 1 | 2 | 2 | 1 | 2 | 2 | 1 | 33.912
Nos of Sheets
Tank | 6 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
| Thickness | Width | Length | Description | Qty | CSA | WEIGHT
Stay rod | 10 | - | 737 | 10mm BS Rod | 0 | 79
Tie Rod | 10 | - | 284 | 10mm BS Rod | 4 | 79
Flange Long side | 6 | 50 | 1131 | 50x50x6 Angle Iron | 2 | 564 | 10.0148
Flange Short side | 6 | 50 | 483 | 50x50x6 Angle Iron | 2 | 564 | 4.2769 |  |  |  | cons
Traverse-Horizontal | 10 | 75 | 194 | 75x10 Flat Iron | 0 | 750 | 0
Traverse-Vertical | 10 | 75 | 245 | 75x10 Flat Iron | 0 | 750 | 0
Foot | 10 | 75 | 384 | 75x10 Flat Iron | 2 | 750 | 4.5216
Base Skid | - | 76 | 800 | 76x38x6 MS Channel | 2 | 840 | 10.5504
Steel Channel | 4 | 217 | 1021 | 4 mm MS Plate | 4 | 868 | 27.8276
Wooden cross cut height | 10 | 52 | 820 | 0 | 0 | 520
Wooden clamp height | 120 | 25 | 1011 | 0 | 0 | 3000
COOLING
Panel Radiators | NO | 18
700/ 700/ 700/ 700 | 5 | 10 | 0
No of radiators | 0
Elements/radiator | 700/
Center to center distance | 0
Depth of a radiator | #VALUE!
Width of radiator flange | 150
Radiator width | 520
Distance bet 2 radiators | 80
Offset for off-central type | 131
PANEL TYPE RADS | LV | HV | Cons. Side | Other Side | Length Addition | Width Addition
1 | 1 | 0 | 0 | 0 | 0 | #VALUE!
1 | 2 | 0 | 0 | 0 | 0 | #VALUE!
3 | 2 | 1 | 0 | 0 | 0 | #VALUE!
4 | 2 | 2 | 0 | 0 | 0 | #VALUE!
5 | 2 | 2 | 1 | 0 | #VALUE! | #VALUE!
6 | 2 | 2 | 2 | 0 | #VALUE! | #VALUE!
7 | 2 | 2 | 2 | 1 | #VALUE! | #VALUE!
8 | 2 | 2 | 2 | 2 | #VALUE! | #VALUE!
Fin depth-long side | 120 | 9 | 4
Fin depth-short side | 120
Fin height | 700 | 4
Fin Thickness | 700 | 1.2 | 1.2 | 10 | 5
Labour Hours |  |  | 0 | #REF!
| 10 |  |  | 0
| 10 |  |  | 0
#REF!
ACCESSORIES
HV Bushings | Plug-in Type 36 kV 250 A Interface B |  |  | 150 | 3 | 5 | 3
170 | 36 | 170 | 250 |  |  |  | 4
Selection | Voltage (kV) | BIL (kV) | Current (A) | Height (mm) | Description | Weight (kg)
0 | 12 | 75 | 250 | 310 | 10 NF 250 CD = 305 mm | 5.65
0 | 12 | 75 | 630 | 342 | 10 NF 630 | 8
0 | 12 | 75 | 250 | 150 | 1M (B9722) | 5
0 | 24 | 125 | 250 | 310 | 24 NF 250 P3 CD = 605 mm | 5.65
0 | 24 | 125 | 250 | 150 | Plug-in Type 24 kV 250 A Interface B | 5
0 | 24 | 125 | 630 | 150 | Plug-in Type 24 kV 630 A Interface C | 6.5
0 | 36 | 200 | 250 | 520 | 30 NF 250 CD = 900 mm | 9.35
0 | 36 | 200 | 250 | 520 | 30 NF 250 CD = 1116 mm | 12.55
0 | 36 | 200 | 250 | 520 | 30 NF 250 CD = 1920 mm | 12.55
1 | 36 | 170 | 250 | 150 | Plug-in Type 36 kV 250 A Interface B | 5
0 | 36 | 170 | 630 | 150 | Plug-in Type 36 kV 630 A Interface C | 6.5
0 | 52 | 250 | 1000 | 150 | Plug-in Type 52 kV 1000 A Interface F | 8
0 | 42 | 200 | 250 | 500 | 40 NF 250 | 15
0 | 52 | 250 | 1000 | 730 | 52 NF 1000 CD = 1430 mm | 35.2
LV Bushings | EN 630 |  | 165 | 1.16 | 4 |  | 3
417.362 | 1 | 630 |  |  |  |  | 4
Selection | Voltage (kV) | Current (A) | Height (mm) | Weight (kg) | Description |  | 6
8
0 | 1 | 250 | 120 | 0.43 | EN 250 | 250
1 | 1 | 630 | 165 | 1.16 | EN 630 | 630
0 | 1 | 1250 | 177 | 2.73 | EN 1250 | 1250
0 | 1 | 2000 | 240 | 6.24 | EN 2000 | 2000
0 | 1 | 2500 | 177 | 2.73 | EN 1250 | 1250
0 | 1 | 3150 | 250 | 8.45 | EN 3150 | 3150
0 | 1 | 4000 | 240 | 6.24 | EN 2000 | 2000
0 | 1 | 6300 | 250 | 8.45 | EN 3150 | 3150
0 | 12 | 250 | 310 | 5.65 | 10 NF 250 | 250
0 | 12 | 630 | 310 | 8 | 10 NF 630 | 630
0 | 12 | 250 | 150 | 5 | 1M (B9722) | 250
0 | 24 | 250 | 150 | 5 | Plug-in Type 24 kV 250 A Interface B | 250
0 | 24 | 630 | 150 | 6.5 | Plug-in Type 24 kV 630 A Interface C | 630
Tap selector | HR 7A3.335 (30kV 30A 100mm 5 Pos) | [5 empty] | 0
0 | 30 | 30 | 200 | 5 |  |  | 1
Selection | Voltage (kV) | Current (A) | BIL (kV) | Positions | Description
0 | 20 | 30 | 95 | 5 | HR 7A3.235 (20kV 30A 100mm 5 Pos)
0 | 20 | 30 | 95 | 7 | HR 7A3.235 (20kV 30A 100mm 7 Pos)
0 | 20 | 63 | 95 | 5 | HM 25.43.885 (20kV 63A 131mm 5 Pos)
0 | 20 | 120 | 95 | 5 | HM 28.43.885 (20kV 120A 131mm 5 Pos)
0 | 20 | 250 | 95 | 5 | HM 28.43.885 (20kV 250A 131mm 5 Pos)
1 | 30 | 30 | 200 | 5 | HR 7A3.335 (30kV 30A 100mm 5 Pos)
0 | 30 | 30 | 200 | 7 | HR 7A3.335 (30kV 30A 100mm 7 Pos)
0 | 30 | 30 | 200 | 5 | HM 23.44.885 (30kV 30A 131mm 5 Pos)
0 | 30 | 30 | 200 | 7 | HM 23.44.885 (30kV 30A 131mm 7 Pos)
0 | 30 | 63 | 200 | 5 | HM 25.44.885 (30kV 63A 131mm 5 Pos)
Valves
PRV T-10K1 1R"
PRV T-50 0.4 BAR
DRAIN VALVE NW 22
AIR RELEASE PLUG
ARES DIN25 DOUBLE FLANGE GATE VALVE
SINGLE FLANGE BALL VALVE 1" NW25S-SS
THROTTLE VALVE FOR RADIATOR NW80 FORMB
BALL VALVE 1" PELGER
GATE VALVE WITH SAMPLING
GATE VALVE WITHOUT SAMPLING
SAMPLING VALVE
BALL VALVE 1" Threaded on both sides
Oil Level Indicators
Magnetic- with 400mm boss
Magnetic- with 200mm boss
4 HOLES PRISMATIC
6 HOLES PRISMATIC
8 HOLES PRISMATIC
FLOATING TYPE
VIAT SO4 - Dial Type with Contacts
VIAT SO6 - Dial Type with Contacts
Cable Boxes | [5 empty] | HV Cable Boxes | Selection | Price | Depth | Width | H above cover | Weight
HV CABLE BOX | 0 |  |  |  |  | Plug-In Cable Box | 0 | 350 | 1052 | 747 | 391 | 100
LV CABLE BOX | 600 |  |  |  |  | 1M Cable Box | 0 | 350 | 862 | 578 | 318 | 57
WTI BOX | 0
CONNECTOR BOX | 0 |  |  |  |  | LV Cable Boxes |  | Price | Depth | Width | H above cover | Weight
HV ENCLOSURE | 0 |  |  |  |  | EN 250 | 0 | 500 | 933 | 770 | 331 | 85
Other Parts | [5 empty] | EN 630 | 1 | 600 | 933 | 770 | 331 | 135
RATING PLATE | [5 empty] | EN 1250 | 0 | 700 | 1085 | 1073 | 386 | 150
PHASE MARKING PLATES | [5 empty] | EN 1250 x 2 | 0 | 750 | 1085 | 1073 | 386 | 180
S/A MOUNTING BRACKET A-2 | [5 empty] | EN 2000 | 0 | 800 | 1065 | 1115 | 431 | 200
ISD UNIT | [5 empty] | EN 2000 x 2 | 0 | 850 | 1420 | 1115 | 431 | 230
BREATHER 1KG TYPE A | [5 empty] | EN 3150 | 0 | 900 | 1140 | 1185 | 518 | 300
BREATHER 1KG TYPE B | [5 empty] | EN 3150 x 2 | 0 | 950 | 1495 | 1133 | 518 | 340
BREATHER 1KG TYPE C
BREATHER 2KG | [5 empty] | WTI Box | 0 | 250 | 400 | 700 | 500 | 10
THERMOMETER TEK 16 | [5 empty] | Connector Box | 0 | 150 | 300 | 500 | 300 | 5
THERMOWELL 3/4" BSP | [5 empty] | HV Enclosure | 0 | 250 | 630 | 750 | 400 | 15
THERMOMETER POCKET
GALVANIZED CUP FOR THERMOMETER POCKET
BUCHOLZ RELAY EW712
CONSERVATOR FILLING CAP AL. 2"
T/F WHEEL 7613T00691 |  |  |  | SDF |  | HRC Fuse
T/F WHEEL 7613T00691 |  |  |  | Current | 630 | 500
WINDING TEMP. INDICATOR TD50 (354 01 12X6.0) |  |  |  | 20 | 20A 3KL81113HA10
WINDING TEMP. INDICATOR TD76 (354 01 12X6.0) |  |  |  | 32 | 32A 3KL81213HA10
RTD WTI (PT100) |  |  |  | 63 | 63A 3KL81513HA10
RTD OTI (PT100) |  |  |  | 100 | 100A 3KL82113HA10
CT 3000/2A Oil Immersed (Measuring) Ring Type 15VA/0.5 |  |  |  | 125 | 125A 3KL82213HA10
CT 5000/5A Oil Immersed (Measuring) Ring Type 15VA/0.5 |  |  |  | 160 | 160A 3KL82313HA10
CT 1600/1A 5P20 15VA/0.5 2 Core |  |  |  | 200 | 200A 3KL83113HA10
NCT 400/1A 5P20 15VA |  |  |  | 250 | 250A 3KL83213HA10
NCT 1600/1A 5P20 15VA |  |  |  | 315 | 315A 3KL83313HA10
NCT 2000/1A 5P20 15VA |  |  |  | 400 | 400A 3KL83413HA10
CT TERMINAL BOX (2 TERMINALS) |  |  |  | 500 | 500A 3KL84113HA10
CT TERMINAL BOX (4 TERMINALS) |  |  |  | 630 | 630A 3KL84213HA10
CT TERMINAL BOX (6 TERMINALS) |  |  |  | 800 | 800A 3KL84313HA10
24kV ELBOW CONNECTOR SET (03)
36kV ELBOW CONNECTOR SET (03)
52kV ELBOW CONNECTOR SET (04)
OBO SURGE ARRESTERS
LTL Name Board
Nut, Bolt & 2 Washers (Galvanized) M10 x 40 mm
Split washers for tank cover fixing
M12 bolt, nut, spring washer & lock washer for earthing terminal
Flange Gasket
Wooden Pallete For Packing
Painting |  |  |  |  | Capacity | 2 Coat Sys - DFT 130 |  | 3 Coat Sys - DFT 250
GALVANIZING |  |  | 172.12 |  | 800 | Primer (kg) | Powder (kg) | Primer (kg) | Powder (kg)
PRIMER PAINT & THINNER |  |  | 10 |  | 250 | 5 | 6 | 10 | 6
POWDER PAINT (RAL6028) |  |  | 15 |  | 800 | 10 | 15 | 20 | 15 |  | 20
INTERNAL PAINT |  |  | 10 |  | 1250 | 15 | 20 | 30 | 20
[5 empty] | 2000 | 20 | 30 | 40 | 30
Cooling Ducts |  |  |  |  | 2500 | 25 | 30 | 50 | 30
LV No. of Cooling Ducts | 0.67 |  |  |  | 3150 | 30 | 40 | 60 | 40
LV MTL | 657.806 |  |  |  | 4000 | 40 | 50 | 70 | 50
LV No. of Layers | 26 |  |  |  | 5000 | 50 | 60 | 80 | 60
LV Cooling duct height | 348
| 0.33 | 13 |  |  | 1/3 Cooling Duct Between Layers 13 & 14 (348 x 220 mm)
| 0.67 | 13 |  |  | 2/3 Cooling Duct Between Layers 13 & 14 (348 x 440 mm)
| 1 | 13 |  |  | Full Cooling Duct Between Layers 13 & 14 (348 x 660 mm)
| 1.33 | 11 | 18 |  | Full Cooling Duct Between Layers 11 & 12 (348 x 590 mm) | 1/3 Cooling Duct Between Layers 18 & 19 (348 x 240 mm)
| 1.67 | 9 | 17 |  | Full Cooling Duct Between Layers 9 & 10 (348 x 590 mm) | 2/3 Cooling Duct Between Layers 17 & 18 (348 x 480 mm)
| 2 | 8 | 17 |  | Full Cooling Duct Between Layers 8 & 9 (348 x 590 mm) | Full Cooling Duct Between Layers 17 & 18 (348 x 720 mm)
| 2.33 | 7 | 15 | 20 | Full Cooling Duct Between Layers 7 & 8 (348 x 560 mm) | Full Cooling Duct Between Layers 15 & 16 (348 x 660 mm) | 1/3 Cooling Duct Between Layers 20 & 21 (348 x 250 mm)
| 2.67 | 7 | 14 | 20 | Full Cooling Duct Between Layers 7 & 8 (348 x 560 mm) | Full Cooling Duct Between Layers 14 & 15 (348 x 660 mm) | 2/3 Cooling Duct Between Layers 20 & 21 (348 x 500 mm)
| 3 | 6 | 13 | 19 | Full Cooling Duct Between Layers 6 & 7 (348 x 560 mm) | Full Cooling Duct Between Layers 13 & 14 (348 x 660 mm) | Full Cooling Duct Between Layers 19 & 20 (348 x 760 mm)
HV No. of Cooling Ducts | 1
HV MTL | 946.6
HV No. of Layers | 17
HV Cooling duct height | 348
| 0.33 | 8 |  |  | 1/3 Cooling Duct Between Layers 8 & 9 (348 x 320 mm)
| 0.67 | 8 |  |  | 2/3 Cooling Duct Between Layers 8 & 9 (348 x 630 mm)
| 1 | 8 |  |  | Full Cooling Duct Between Layers 8 & 9 (348 x 950 mm)
| 1.33 | 7 | 12 |  | Full Cooling Duct Between Layers 7 & 8 (348 x 850 mm) | 1/3 Cooling Duct Between Layers 12 & 13 (348 x 350 mm)
| 1.67 | 6 | 11 |  | Full Cooling Duct Between Layers 6 & 7 (348 x 850 mm) | 2/3 Cooling Duct Between Layers 11 & 12 (348 x 690 mm)
| 2 | 5 | 11 |  | Full Cooling Duct Between Layers 5 & 6 (348 x 850 mm) | Full Cooling Duct Between Layers 11 & 12 (348 x 1040 mm)
| 2.33 | 5 | 10 | 13 | Full Cooling Duct Between Layers 5 & 6 (348 x 800 mm) | Full Cooling Duct Between Layers 10 & 11 (348 x 950 mm) | 1/3 Cooling Duct Between Layers 13 & 14 (348 x 360 mm)
| 2.67 | 4 | 9 | 13 | Full Cooling Duct Between Layers 5 & 5 (348 x 800 mm) | Full Cooling Duct Between Layers 9 & 10 (348 x 950 mm) | 2/3 Cooling Duct Between Layers 13 & 14 (348 x 730 mm)
| 3 | 4 | 8 | 12 | Full Cooling Duct Between Layers 4 & 5 (348 x 800 mm) | Full Cooling Duct Between Layers 8 & 9 (348 x 950 mm) | Full Cooling Duct Between Layers 12 & 13 (348 x 1090 mm)
Note on D81: Eranga: VALUE(LEFT(P!C82,FIND(".",P!C82,1)-1))
Note on D82: Eranga: VALUE(LEFT(P!C83,FIND(".",P!C83,1)-1))
Note on B83: Eranga: =ROUNDUP(C79*100,2)
Note on B84: Eranga: =MROUND(D80*C80+2,5)
Note on B85: Eranga: =MROUND(D81*C81/B84+2,5)
Note on C140: Eranga Anuradha Bala: =IF(AND(B47<30000,B46<=400),B134-2,IF(VALUE(B134)<611,B134,MROUND(B134-3,5)))
Note on G153: Eranga: Double foil 0.15 DL x 2
Note on G211: Eranga: Axial Parallel

## Bill of Materials
Bill of Materials
Transformer Type: |  | 300kVA 33000/415V
Contract No.:
Customer: |  | Ceylex
No of Transformers: |  | 2
| Material | Description | Unit | Qty | Unit Price | Cost | % | Total Quantity | Per Winding Quantity
| MAJOR MATERIALS |  |  | xxx
1 | Oil | Inhibited Mineral Oil | L | 367.8161 | 1.3 | 478.1609 | 5.691% | 735.6322
2
LV Winding
3 | LV Conductor | 330 x 0.275 x 2 | kg | 83.44 | 10.36 | 864.4384 | 10.29% | 166.88 | 27.8133
4 | Flat Copper | 4*38mm | kg | 7.77 | 10.3 | 80.031 | 0.9525% | 15.54 | 2.59
5 | DDP Double Layer | 348mm x 0.15 DDP DL | kg | 3.89 | 8.78 | 34.1542 | 0.4065% | 7.78 | 1.2967
6 | DDP Single Layer | 348mm x 0.15 DDP SL | kg | 0 | 5.59 | 0 | 0% | 0 | 0
7 | DDP Single Layer | 348mm x 0.25 DDP SL | kg | 0 | 4.42 | 0 | 0% | 0 | 0
8 | LV Edge Strip | 8 x 0.25mm | kg | 0.44126 | 4.95 | 2.1842 | 0.026% | 0.88251 | 0.14709
9 | LV Insulation Packet | 300/33 INLV | Nos. | 3 | 5.2 | 15.6 | 0.1857% | 6
10 | [5 empty] | 0 | 0% | 0
HV Winding
11 | HV Conductor | 1.150mm CU-Round | kg | 99.38 | 10.41 | 1034.5458 | 12.31% | 198.76 | 33.1267
12 | DDP Single Layer | 348mm x 0.15 DDP SL | kg | 0 | 5.59 | 0 | 0% | 0 | 0
13 | DDP Single Layer | 348mm x 0.25 DDP SL | kg | 0.75 | 4.36 | 3.27 | 0.03892% | 1.5 | 0.25
14 | HV Strip Insulation | 33 x 0.05 mm Strip | kg | 18.9912 | 4.76 | 90.3981 | 1.076% | 37.9824 | 6.3304
15 | HV Edge Strip | 33 x 0.25mm | kg | 0 | 6.26 | 0 | 0% | 0 | 0
16 | HV Insulation Packet | 300/33 INHV | Nos. | 3 | 65 | 195 | 2.321% | 6
17
Assembly
18 | HD Copper | 3 mm | kg | 5.3333 | 13.13 | 70.0267 | 0.8334% | 10.6667
19 | Bare Copper | 7/1.7 mm | kg | 0 | 7.65 | 0 | 0% | 0
20 | Bare Copper | 19/1.35 mm | kg | 0 | 7.65 | 0 | 0% | 0
21 | Copper Flexible | 300/33 CUFX | Nos. | 4 | 20.84 | 83.36 | 0.9921% | 8
22 | Timber Packet | 300/33 TMBC & TMAS | Nos. | 1 | 51 | 51 | 0.607% | 2
23 | Insulation Packet | 300/33 INBC & INAS | Nos. | 1 | 160 | 160 | 1.904% | 2
24 | Assembly Packets (Core+Tanking+Dispatch) |  | Nos. | 1 | 25 | 25 | 0.2975% | 2
24 | Copper Assembly |  | kg | 5 | 11 | 55 | 0.6546% | 10
| CORE STEEL |  | kg | 515.4 | 3.97 | 2046.138 | 24.35% | 1030.8
21 | 23ZDKH85 | 150mm | kg | 188.6 |  | 0 | 0% | 377.2
22 | 23ZDKH85 | 140mm | kg | 159.7 | 0 | 0 | 0% | 319.4 |  | General Choice
23 | 23ZDKH85 | 120mm | kg | 90.5 | 0 | 0 | 0% | 181 |  | #N/A | 300/33/415 EU CU | CU
24 | 23ZDKH85 | 100mm | kg | 45.9 | 0 | 0 | 0% | 91.8
25 | 23ZDKH85 | 70mm | kg | 30.8 | 0 | 0 | 0% | 61.6 |  | Custom Choice
26 | 0 | 0 | kg | 0 | 0 | 0 | 0% | 0
27 | 0 | 0 | kg | 0 | 0 | 0 | 0% | 0
28 | 0 | 0 | kg | 0 | 0 | 0 | 0% | 0
29 | 0 | 0 | kg | 0 | 0 | 0 | 0% | 0
| STEEL |  |  | xxx | [5 empty] | Special Requirements
30 | Tank Steel, Trava, Foot & Clamps |  | kg | 71 | 2.64 | 187.44 | 2.231% | 142 |  | Cover Plate Thickness
31 | Fin Type Radiators | 300/33/415 Tank | kg | 261.2 | 3.89 | 1016.068 | 12.09% | 522.4 |  | Base Thickness
32 | Pole Mounting Bracket |  | Nos. |  |  | 0 | 0% | 0
33 | [9 empty] | Tank Wall Thickness
| ACCESSORIES |  |  | xxx
HV Bushings
33 | Plug-in Type 36 kV 250 A Interface B |  | Nos. | 3 | 43 | 129 | 1.535% | 6
34 | HV Cable connectors |  | Nos. | 3 | 15 | 45 | 0.5356% | 6
| LV Bushings |  |  |  |  | 0 | 0%
35 | EN 630 |  | Nos. | 4 | 25.88 | 103.52 | 1.232% | 8
36 | LV Cable Lugs |  | Nos. |  |  | 0 | 0% | 0
| Tap selector |  |  |  |  | 0 | 0%
37 | HR 7A3.335 (30kV 30A 100mm 5 Pos) |  | Nos. | 1 | 34.45 | 34.45 | 0.41% | 2
38
| Valves |  |  |  |  | 0 | 0%
39 | PRV T-10K1 1R" |  | Nos. | 1 | 7.4 | 7.4 | 0.08807% | 2
40 | PRV T-50 0.4 BAR |  | Nos. |  |  | 0 | 0% | 0
41 | DRAIN VALVE NW 22 |  | Nos. | 1 | 11.96 | 11.96 | 0.1423% | 2
42 | AIR RELEASE PLUG |  | Nos. |  |  | 0 | 0% | 0
43 | ARES DIN25 DOUBLE FLANGE GATE VALVE |  | Nos. |  |  | 0 | 0% | 0
44 | SINGLE FLANGE BALL VALVE 1" NW25S-SS |  | Nos. |  |  | 0 | 0% | 0
45 | THROTTLE VALVE FOR RADIATOR NW80 FORMB |  | Nos. | 0 |  | 0 | 0% | 0
46 | BALL VALVE 1" PELGER |  | Nos. | 0 |  | 0 | 0% | 0
47 | GATE VALVE WITH SAMPLING |  | Nos. |  | 165 | 0 | 0% | 0
48 | GATE VALVE WITHOUT SAMPLING |  | Nos. | 0 |  | 0 | 0% | 0
49 | SAMPLING VALVE |  | Nos. |  |  | 0 | 0% | 0
50 | BALL VALVE 1" Threaded on both sides |  | Nos. |  |  | 0 | 0% | 0
51 | [5 empty] | 0 | 0% | 0
| Oil Level Indicators |  |  |  |  | 0 | 0%
52 | Magnetic- with 400mm boss |  | Nos. | 0 |  | 0 | 0% | 0
53 | Magnetic- with 200mm boss |  | Nos. |  | 24.85 | 0 | 0% | 0
54 | 4 HOLES PRISMATIC |  | Nos. |  | 10.25 | 0 | 0% | 0
55 | 6 HOLES PRISMATIC |  | Nos. |  | 13.66 | 0 | 0% | 0
56 | 8 HOLES PRISMATIC |  | Nos. |  | 15.31 | 0 | 0% | 0
57 | FLOATING TYPE |  | Nos. |  | 6.33 | 0 | 0% | 0
58 | VIAT SO4 - Dial Type with Contacts |  | Nos. |  | 111.82 | 0 | 0%
59 | VIAT SO6 - Dial Type with Contacts |  | Nos. |  | 158.13 | 0 | 0%
60 | [5 empty] | 0 | 0%
| Cable Boxes |  |  |  |  | 0 | 0%
61 | HV CABLE BOX |  | Nos. |  | 0 | 0 | 0% | 0
62 | LV CABLE BOX |  | Nos. | 1 | 800 | 800 | 9.521% | 2
63 | WTI BOX |  | Nos. |  | 0 | 0 | 0% | 0
64 | CONNECTOR BOX |  | Nos. |  | 0 | 0 | 0% | 0
65 | HV ENCLOSURE |  | Nos. |  | 0 | 0 | 0% | 0
66
| Other Parts |  |  |  |  | 0 | 0%
67 | RATING PLATE |  | Nos. | 1 | 4.87 | 4.87 | 0.05796% | 2
68 | PHASE MARKING PLATES |  | Nos. | 1 | 2.4865 | 2.4865 | 0.02959% | 2
69 | S/A MOUNTING BRACKET A-2 |  | Nos. | 1 | 15.42 | 15.42 | 0.1835% | 2
70 | ISD UNIT |  | Nos. | 1 | 308 | 308 | 3.666% | 2
71 | BREATHER 1KG TYPE A |  | Nos. | 0 | 17.37 | 0 | 0% | 0
72 | BREATHER 1KG TYPE B |  | Nos. | 0 | 21.7125 | 0 | 0% | 0
73 | BREATHER 1KG TYPE C |  | Nos. |  | 18.6107 | 0 | 0% | 0
74 | BREATHER 2KG |  | Nos. | 0 |  | 0 | 0% | 0
75 | THERMOMETER TEK 16 |  | Nos. | 0 |  | 0 | 0% | 0
76 | THERMOWELL 3/4" BSP |  | Nos. |  | 10 | 0 | 0% | 0
77 | THERMOMETER POCKET |  | Nos. | 1 | 2.5 | 2.5 | 0.02975% | 2
78 | GALVANIZED CUP FOR THERMOMETER POCKET |  | Nos. | 1 | 2.5 | 2.5 | 0.02975% | 2
79 | BUCHOLZ RELAY EW712 |  | Nos. | 0 |  | 0 | 0% | 0
80 | CONSERVATOR FILLING CAP AL. 2" |  | Nos. | 0 |  | 0 | 0% | 0
81 | T/F WHEEL 7613T00691 |  | Nos. |  | 35.33 | 0 | 0% | 0
82 | T/F WHEEL 7613T00691 |  | Nos. |  |  | 0 | 0% | 0
83 | WINDING TEMP. INDICATOR TD50 (354 01 12X6.0) |  | Nos. |  |  | 0 | 0% | 0
84 | WINDING TEMP. INDICATOR TD76 (354 01 12X6.0) |  | Nos. |  | 1654.08 | 0 | 0% | 0
85 | RTD WTI (PT100) |  | Sets. |  |  | 0 | 0% | 0
86 | RTD OTI (PT100) |  | Sets. |  |  | 0 | 0% | 0
87 | CT 3000/2A Oil Immersed (Measuring) Ring Type 15VA/0.5 |  | Nos. |  | 50 | 0 | 0% | 0
88 | CT 5000/5A Oil Immersed (Measuring) Ring Type 15VA/0.5 |  | Nos. |  | 60 | 0 | 0% | 0
89 | CT 1600/1A 5P20 15VA/0.5 2 Core |  | Nos. |  | 170.1 | 0 | 0% | 0
90 | NCT 400/1A 5P20 15VA |  | Nos. |  | 235.305 | 0 | 0% | 0
91 | NCT 1600/1A 5P20 15VA |  | Nos. |  | 88.95 | 0 | 0% | 0
92 | NCT 2000/1A 5P20 15VA |  | Nos. |  | 297.675 | 0 | 0% | 0
93 | CT TERMINAL BOX (2 TERMINALS) |  | Nos. |  | 55.04 | 0 | 0% | 0
94 | CT TERMINAL BOX (4 TERMINALS) |  | Nos. |  | 50 | 0 | 0% | 0
95 | CT TERMINAL BOX (6 TERMINALS) |  | Nos. |  |  | 0 | 0% | 0
96 | 24kV ELBOW CONNECTOR SET (03) |  | Nos. | 0 |  | 0 | 0% | 0
97 | 36kV ELBOW CONNECTOR SET (03) |  | Nos. | 0 |  | 0 | 0% | 0
98 | 52kV ELBOW CONNECTOR SET (04) |  | Nos. | 0 |  | 0 | 0% | 0
99 | OBO SURGE ARRESTERS |  | Nos. | 0 |  | 0 | 0% | 0
100 | LTL Name Board |  | Nos. |  | 7.027 | 0 | 0% | 0
101 | Nut, Bolt & 2 Washers (Galvanized) M10 x 40 mm |  | Nos. |  |  | 0 | 0% | 0
102 | Split washers for tank cover fixing |  | Nos. |  |  | 0 | 0% | 0
103 | M12 bolt, nut, spring washer & lock washer for earthing terminal |  | Nos. |  |  | 0 | 0% | 0
104 | MCCB |  | Nos. | 0 | 0 | 0 | 0% | 0
105 | Surge arresters |  | Nos. | 3 | 14.47 | 43.41 | 0.5166% | 6
105 |  |  | Nos. | 0 |  | 0 | 0% | 0
| Painting |  |  |  |  | 0 | 0%
106 | GALVANIZING |  | kg |  | 0.30843 | 0 | 0% | 0
107 | PRIMER PAINT & THINNER |  | kg |  | 9.2 | 0 | 0% | 0
108 | POWDER PAINT (RAL6028) |  | kg |  | 7.37 | 0 | 0% | 0
109 | INTERNAL PAINT |  | kg |  | 7.6837 | 0 | 0% | 0
| 0 |  |  | 0 |  | 0 | 0% | 0
| Major Material |  | $ | * * * |  | 6491.8153 | 77.26% | 12983.6307
| Accessories |  | $ | * * * |  | 1510.5165 | 17.98% | 3021.033
| Miscellaneous |  | $ | * * * | 5% | 400.1166 | 4.762% | 800.2332
| Total Materials |  | $ | * * * |  | 8402.4484 | #DIV/0! | 16804.8969
Design Engineer
-
Note on L45: Eranga: If different radiator is used, type it here.

## Radiator Choise
Standard Copper EU2021 Radiators | 1000/33/415 EU | 1000/33/415 EU Tank
| 1000/33/400 EU | 1250/33/415 EU Tank
| 1000/33/440 EU | 1250/33/415 EU Tank
| 1000/33/690 EU | 1250/33/415 EU Tank
| 1000/33/800 EU | 1250/33/415 EU Tank
| 1250/33/415 EU | 1250/33/415 EU Tank
| 1250/33/400 EU | 1250/33/400 EU Tank
| 1250/33/440 EU | 1250/33/400 EU Tank
| 1250/33/690 EU | 1250/33/400 EU Tank
| 1250/33/800 EU | 1250/33/400 EU Tank
| 1600/33/415 EU | 1600/33/400 EU Tank
| 1600/33/400 EU | 1600/33/400 EU Tank
| 1600/33/440 EU | 1600/33/400 EU Tank
| 1600/33/690 EU | 1600/33/400 EU Tank
| 1600/33/800 EU | 1600/33/400 EU Tank
| 2000/33/415 EU | 2000/33/400 EU Tank
| 2000/33/400 EU | 2000/33/400 EU Tank
| 2000/33/440 EU | 2000/33/400 EU Tank
| 2000/33/690 EU | 2000/33/400 EU Tank
| 2000/33/800 EU | 2000/33/400 EU Tank
| 2500/33/415 EU | 2500/33/400 EU Tank
| 2500/33/400 EU | 2500/33/400 EU Tank
| 2500/33/440 EU | 2500/33/400 EU Tank
| 2500/33/690 EU | 3150/33/415 EU Tank
| 2500/33/800 EU | 2500/33/400 EU Tank
| 3150/33/415 EU | 3150/33/415 EU Tank
| 3150/33/400 EU | 3150/33/415 EU Tank
| 3150/33/440 EU | 3150/33/415 EU Tank
| 3150/33/690 EU | 3150/33/415 EU Tank
| 3150/33/800 EU | 3150/33/415 EU Tank
Standard Aluminium EU2021 Radiators | 1000/33/415 EU AL | 1250/33/400 EU AL Tank
| 1000/33/400 EU AL | 1250/33/400 EU AL Tank
| 1000/33/440 EU AL | 1250/33/400 EU AL Tank
| 1000/33/690 EU AL | 1250/33/400 EU AL Tank
| 1000/33/800 EU AL | 1250/33/400 EU AL Tank
| 1250/33/415 EU AL | 1250/33/400 EU AL Tank
| 1250/33/400 EU AL | 1250/33/400 EU AL Tank
| 1250/33/440 EU AL | 1250/33/400 EU AL Tank
| 1250/33/690 EU AL | 1250/33/400 EU AL Tank
| 1250/33/800 EU AL | 1250/33/400 EU AL Tank
| 1600/33/415 EU AL | 2000/33/400 EU AL Tank
| 1600/33/400 EU AL | 2000/33/400 EU AL Tank
| 1600/33/440 EU AL | 2000/33/400 EU AL Tank
| 1600/33/690 EU AL | 2000/33/400 EU AL Tank
| 1600/33/800 EU AL | 2000/33/400 EU AL Tank
| 2000/33/415 EU AL | 2000/33/400 EU AL Tank
| 2000/33/400 EU AL | 2000/33/400 EU AL Tank
| 2000/33/440 EU AL | 2000/33/400 EU AL Tank
| 2000/33/690 EU AL | 2000/33/400 EU AL Tank
| 2000/33/800 EU AL | 2000/33/400 EU AL Tank
| 2500/33/415 EU AL | 2500/33/400 EU AL Tank
| 2500/33/400 EU AL | 2500/33/400 EU AL Tank
| 2500/33/440 EU AL | 2500/33/400 EU AL Tank
| 2500/33/690 EU AL | 3150/33/400 EU AL Tank
| 2500/33/800 EU AL | 2500/33/400 EU AL Tank
| 3150/33/415 EU AL | 3150/33/400 EU AL Tank
| 3150/33/400 EU AL | 3150/33/400 EU AL Tank
| 3150/33/440 EU AL | 3150/33/400 EU AL Tank
| 3150/33/690 EU AL | 3150/33/400 EU AL Tank
| 3150/33/800 EU AL | 3150/33/400 EU AL Tank
Standard CEB Cu EU2021 Radiators | 100/33/415 EU CU | 160/33/415 EU CU Tank
| 160/33/415 EU CU | 160/33/415 EU CU Tank
| 250/33/415 EU CU | 250/33/415 EU CU Tank
| 400/33/415 EU CU | 400/33/415 EU CU Tank
| 630/33/415 EU CU | 630/33/415 EU CU Tank
| 800/33/415 EU CU | 800/33/415 EU CU Tank
| 1000/33/415 EU CU | 1000/33/415 EU CU Tank
| 100/11/415 EU CU | 100/11/415 EU CU Tank
| 160/11/415 EU CU | 160/11/415 EU CU Tank
| 250/11/415 EU CU | 250/11/415 EU CU Tank
| 400/11/415 EU CU | 400/11/415 EU CU Tank
| 630/11/415 EU CU | 630/11/415 EU CU Tank
| 800/11/415 EU CU | 800/11/415 EU CU Tank
| 1000/11/415 EU CU | 1000/11/415 EU CU Tank

## Techspecs
LTL TRANSFORMERS (PVT) LTD FRM/CI/02
Transformer Technical Specifications
Customer | Ceylex
Project: | Ceylex
Contract/Quotation No. | Quatation |  | Design No: | 30033415 |  |  | Date: | 2023-05-28
Basic Technical Features |  |  | Unit | Customer Requirements |  | Review by LTL |  | Remarks
1. Capacity |  |  | kVA | 300 |  | 300
2. No. of Units required |  |  | Nos. | 1 |  | 1
3. Frequency |  |  | Hz | 50 |  | 50
4. No. of Phases |  |  |  | 3 |  | 3
5. Primary Voltage |  |  | V | 33000 |  | 33000
6. Tappings |  | 1 |  |  |  | 5%
2 | [5 empty] | 2.5%
3 | [5 empty] | 0%
4 | [5 empty] | -2.5%
5 | [5 empty] | -5%
-
-
-
-
7. Secondary Voltage (No Load) |  |  | V | 415 |  | 415
8. Vector Symbol |  |  |  | Dyn11 |  | Dyn11
9. Lightning Impulse Withstand Voltage (Primary / Secondary) |  |  | kV |  |  | 170 / - |  |  |  |  | 33 kV | 0 | 200 / - | 70 / 3
10. Power Frequency Withstand Voltage (Primary / Secondary) |  |  | kV |  |  | 70 / 3 |  |  |  |  | 33 kV | 1 | 170 / - | 70 / 3
11. Conductor Material (Primary / Secondary) |  |  |  | Cu / Cu |  | Cu / Cu
12. Temp. Rise | Windings |  | °C |  |  | 55 |  |  |  |  | 11 kV | 0 | 95 / - | 28 / 3
| Top Oil |  | °C |  |  | 50 |  |  |  |  | 7.2 kV | 0 | 75 / - | 28 / 3
13. Efficiency at 100% load (P.F = 0.8) |  |  | % |  |  | 98.1796 |  |  |  |  | 7.2 kV | 0 | 60 / - | 20 / 3
14. Voltage regulation at 100% load (P.F = 0.8) |  |  | % |  |  | 3.7707 |  |  |  |  | Custom Choise
15. No Load current |  |  | % |  |  | 0.6 |  | IEC Tolerances Applicable
16. Method of cooling | [5 empty] | ONAN
17. No load loss |  |  | W |  |  | 550 |  | IEC Tolerances Applicable
18. Load loss |  |  | W |  |  | 3900 |  | IEC Tolerances Applicable
19. Impedance voltage |  |  | % |  |  | 4.67 |  | IEC Tolerances Applicable
20. Sound level |  |  | dB |  |  | 52
21. Dimensions
| Length |  | mm |  |  | 1236 |  | Approximately
| Width |  | mm |  |  | 1365 |  | Approximately
| Height |  | mm |  |  | 1631 |  | Approximately
22.Total Weight |  |  | kg |  |  | 1440 |  | Approximately
23.Oil Weight |  |  | kg |  |  | 320 |  | Approximately
24.Un-tanking Weight |  |  | kg |  |  | 790 |  | Approximately
25. Availabilty of Cable box in Primary side, Y/N | [5 empty] | Y |  |  | Y
26. Availabilty of Cable box in Secondary side, Y/N | [5 empty] | N |  |  | N
27. Hermetically sealed/Conservator |  |  |  | Hermetically sealed |  | Hermetically sealed |  |  | Includes in ISD | Hermetically sealed |  | Galvanize
28. Painting Method, Galvanize/Marine paint/Powder | [5 empty] | Galvanize |  | C3 |  | Conservator |  | Marine paint
29. Unit Colour | [5 empty] | RAL6028 |  | Dark Green |  |  |  | Powder
30. Service conditions
| Max. ambient temp. |  | °C |  |  | 45
| Monthly average temp. |  | °C |  |  | 35
| Yearly average temp. |  | °C |  |  | 25
31. Altitude (Maximum) |  |  | m |  |  | 1000
32. Standard | [5 empty] | IEC60076:2011
33. Protection Available |  | 34. Changes by customer (if any)
ISD (includes protection for oil level, oil temp.,pressure & gas ) | N
Oil Level Indicator | Y |  | Designation |  | Sig. |  |  | Date
Pressure Release Device (Without Contacts) | Y | Designed by: | EE |  |  |  |  | 2023-05-28
Winding Temperature Indicator | N | Reviewed by: | EE |  |  |  |  | 2023-05-28
Bi- Directional Rollers | N | Approved by: | MDC |  |  |  |  | 2023-05-28
Revision No.: 03/01-12-2015
Note on H42: Eranga: =Q!B114
Note on H43: Eranga: =Q!B115
Note on H44: Eranga: =Q!B116
Note on H45: Eranga: =Q!B117
Note on H46: Eranga: =Q!B118
Note on H47: Eranga: =Q!B120

## DDOS
LTL TRANSFORMERS (PVT.) LTD. FRM/DE/01
DESIGN DATA OUTPUT SHEET
CORE DETAIL |  | B (T) : 1.750 | L (mm) : 62 |  |  | WT. (Kg) |  | L | #REF! | #REF!
V/T : 9.215 | GRADE : 23ZDKH | C - C (mm) : 318 | W1 / W2 / W3 / W4 (mm) : 29.5 / 20 / 17.5 / 11 (HV) / 4 (LV) |  |  |  |  | W1 | #REF! | #REF!
AREA : 237.2 cm2 |  | W - H (mm) : 377 | A (mm) : 194 | H (mm) : 150 |  | 188.6
|  |  |  | T1 / T2 / T3 / T4 (mm) : 140 / 120 / 100 / 70 |  | 159.7 / 90.5 / 45.9 / 30.8
WINDING TYPE |  | LV |  |  | HV
VOLTS (L/PH) V |  | 415 / 239.6 |  |  | 33000 / 33000
CURRENT (L/PH) A |  | 417.362 / 417.362 |  |  | 5.249 / 3.03
CONNECTION |  | yn |  |  | D
TEST (PF / IMP.) kV |  | 3 / - |  |  | 70 / 200 |  |  |  | 70 / 200 | 33 kV
TURNS |  | 26 |  |  | 3760 / 3581 |  |  |  | 70 / 170 | 33 kV |  | L | 3581 | 5 | 12
LAYERS |  | 26 |  |  | 17 |  |  |  | 28 / 75 | 11 kV
TURNS / LAYER |  | 1 |  |  | 229.00/ 96.00 * |  |  |  | 20 / 60 | 7.2 kV
INSULATION |  | (2 x 0.15 SL x 348) DDP Between Layers |  |  | Start Thickness 0.375 mm & End Thickness 1.65 mm |  |  |  | 3 / - | LV
0.075 x 45 Strip
EDGE STRIP (mm) |  | 8 x 0.25mm |  |  | 0.075 x 45 Strip
COOLING DUCT |  | 2/3 Cooling Duct Between Layers 11 & 12 (668 x 294 mm x 2) |  |  | Full Cooling Duct Between Layers 6 & 7 (668 x 1249 mm)
-
COND. SIZE BARE (mm) |  | 330 x 0.275 x 2 |  |  | 1.150
COND SIZE COVD. (mm) |  | 330 x 0.275 x 2 |  |  | 1.233
COND. AREA (mm2) |  | 181.462 |  |  | 1.039
AMPS / mm2 |  | 2.300 |  |  | 2.917
LEAD SIZE (mm) |  | 38.000 / 4.000 |  |  | HD Copper - 3 mm dia paper covered |  | HD Copper - 3 mm dia paper covered
FLEXIBLE SIZE (mm) |  | 38.000 / 4.000 |  |  | HD Copper - 3 mm dia paper covered
RADIALS (mm) |  | 23.88/ 19.38/ 23.88 |  |  | 34.30/ 34.30/ 34.30 |  | 7/1.7 bare copper
I.D/O.D (mm) (without tolerance) |  | 181 x 264 / 230 x 337 |  |  | 266 x 373 / 356 x 473 |  | 19/1.35 bare copper | [7 empty] | 153 | 227.763
ELEC./WDG. LGTH. (mm) |  | 330 / 350.000 |  |  | 282.767 / 350.000 | [9 empty] | 214.661 | 298.424
EQ. MEAN DIAM. (mm) |  | 104.6931 |  |  | 150.6561 | [9 empty] | 191.763 | 296.365
MEAN TURN (m) |  | 657.806 |  |  | 946.6 | [9 empty] | 262.424 | 367.026
WEIGHT TOTAL (Kg) |  | 92.37 |  |  | 115.80 | [9 empty] | 5
RESIST / PH (Ohm) |  | 0.001975 @ 75 C |  |  | 68.4047 @ 75 C
I2R + DIR STRAY (W) |  | 1152 |  |  | 1884
BUSHING |  | EN 630 x 4 |  |  | Plug-in Type 36 kV 250 A Interface B x 3
CLEARANCES | CORE / LV : 1.50x 1.50x 7.00 mm |  | LV/HV : | 18.000 mm | HV/HV : 21.000 mm | YOKE/COVER/BASE : 195 / 41 mm
LV INNER TUBE | 1 mm PB (668 mm x 794 mm) |  | STICK BARRIER : | 18 mm (668 mm x 1098 mm)
[9 empty] | Total | Noinal | No. of tap pos | Deviation
TAP | TURNS | LOSSES | CALCULATED | GUARANTEED |  | WEIGHTS (Kg) |  |  | 3760 | 3581 | 5 | 89.5 | 3402 | 4 | 5
1 | 0 | CAPACITY (kVA) | 300 | 300 | LV CU | 83.44
2 | 3402 |  |  |  | HV CU | 99.38
3 | 3492 | CU LOSS (W) | 3900 @ 75 C | 3900 | CU LEAD / BUSBAR | 7.77
4 | 3581 | FE LOSS (W) | 550 | 550 | TOTAL CU | 190.59
5 | 3581 |  |  |  | CORE | 493.2
6 | 3671 | TOTAL LOSS (W) | 1632 @ 75 C |  | LV INSULATION | 3.89
7 | 3760 | REACTANCE (%) | 4.148 |  | HV INSULATION | 15.84
8 |  | IMPEDANCE (%) | 4.67 | 4.67 | CORE AND WDGS | 711
9 |  | NO LOAD CURRENT (%) | 0.6 |  | OIL WEIGHT | 320
10 |  | T. RISE OIL (°C) | 46.5 | 50 | WEIGHT OF RADIATOR | 101
11 |  | T. RISE WDG. (°C) | 54.6 | 55 | TOTAL WEIGHT | 1270 |  |  | 50.7 | 54.6
12 |  | X/R | 12 |  | EXPANSION OIL VOLUME | 10 L
TANK INSIDE | LENGTH (mm) : 1031 |  |  | WIDTH (mm) : | 483 | HEIGHT (mm) : 913
[5 empty] | CORRUG. L.S DEPTH (mm) : 120 | NO.: 18
HEIGHT OF RADIATOR : |  | 700 |  |  | CORRUG. S.S DEPTH (mm) : 120 | NO.: 8
NUMBER OF RADIATORS : |  |  | CENTER LENGTH OF THE RADIATOR (mm) :
NUMBER OF ELEMENTS PER RADIATOR : |  |  | TYPE OF RADIATOR : |  |  |  | CENTERED
OFF CENTERED
RATING DETAILS
kVA | 300 | VECTOR | Dyn11 | COOLING | ONAN | CONTINUOUS : Y
PHASE | 3 | Hz | 50 | VOLTAGE RATIO : 137.73 |  | TYPE OF UNIT : Hermetically sealed | Hermetically sealed
TAPPINGS ON HV |  | ABOVE NOMINAL : | 2 | IN STEPS OF : 2.5 %
|  | BELOW NOMINAL : | 2 | TAP CHANGER TYPE : HR 7A3.335 (30kV 30A 100mm 5 Pos)
SPECIAL ACCESSORIES: SAMB A-2 |  | / OLI
STANDARD : IEC 60076:2011
CUSTOMER | : Ceylex |  |  | DESIGNED | : | DATE :
DESIGN NO | : 30033415 |  |  | REVIEWED | : | DATE :
CONTRACT NO : | : Quatation |  |  | AUTHORIZED | : | DATE :
Revision:02/01-07-2009
ISD / HV Enclosure 36kV 250A Interface B Plug-in Type Bushings / LV DT3150 Cable Box (6 runs per phase & neutral)