## R
ta File Name: D:\Tr | ial Program\ReportVB | t
* Using Standard Da | ta from Files; Usi | New LTL Core Loss C | alculations ***
TE: 2022.09.15 |  | IQUID TYPE TRANSFOR | MER CALCULATION (Ver | n 6.10.0) |  | Time: 08:16:38
DER : 10033OVL | DESIGN: Data Set 1 | ENGINEER: LASINDU | CUSTOMER NAME | EU
A - 100 Liquid | Type ONAN Cooli | 60 C Rise Th | ree Phase 50 Hz | Style Number:
: 33000 + 2- 2x 2. | 50 % TC: Off-load T | Changer | BIL: 170 (Delt | Line/Coil Amps: |  | 1.750/ 1.010
: 400 |  |  | BIL: 3 (Wye | Line/Coil Amps: |  | 144.338/ 144.338
------------------- | -------------------- | ----- S T A C K E D | C O R E -------- | --------- Width -- |  | Build ----- Weight -
Core Design.......: | OVAL-IY Mitered | Diagonal Dimension: | 130.000 x 202.490 mm | Step 1: 130.000, |  | 72.490 mm 156.8 kg
Grade/Frame Type..: | 23ZDKH / 3-Leg | Window Height.....: | 232.000 mm | Step 2: 120.000, |  | 50.370 mm 99.2 kg
INDUCTION.........: | 1.450 Tesla | Center to Center..: | 293.182 mm | Step 3: 100.000, |  | 32.890 mm 52.5 kg
VPT, W/kg, PBase..: | 6.415, 0.704, 0.53 | Gross/Net CSA.....: | 206.1 / 199.3 cm2 | Step 4: 70.000, |  | 26.450 mm 29.6 kg
100 % Exc Current.: | 0.8241 | Weight of Core-Leg: | 152.1 kg | Step 5: 0.000, |  | 0.000 mm 0.0 kg
Sound/Natural Freq: | 44.9 db / 1978 Hz | Weight of Yoke....: | 169.6 kg | Step 6: 0.000, |  | 0.000 mm 0.0 kg
Peak HV Inrush Cur: | 13 amp | Core Net Weight...: | 321.7 kg | Step 7: 0.000, |  | 0.000 mm 0.0 kg
Utilization Factor: | 0.9080 | Core Scrap Weight.: | 16.4 kg | Step 8: 0.000, |  | 0.000 mm 0.0 kg
Standard Core No..: | NONE STANDARD | Core Gross Weight.: | 338.1 kg | Step 9: 0.000, |  | 0.000 mm 0.0 kg
Ovality Factor....: | 1.402 | Use Max Steel Wi | dth (Steps minus 1) | Using Std | S | teel Widths
Core Perimeter....: | 553.4 mm | Delta Build.......: | 72.5 mm
------------------- | -------------------- | L O W V O L T A | G E W I N D I N G | ------------------ | - | --------------------
Type of Coil......: | CU-Foil | Coil-Length.......: | 205.000 mm | ELECT LENGTH...... | : | 185.000 mm
TURNS PER COIL....: | 1 x 36.0 | Inside Dimensions.: | 133.000 x205.490 mm | Strip-#x#x Wd x Tk | : | 1x1x 185.00 x 0.240
CURRENT DENSITY...: | 3.251 A/mm2 | Outside Dimensions: | 163.490 x240.480 mm | Cond/Lead Weight.. | : | 26.09 / 1.77 kg
|  | Inner Perimeter...: | 562.8 mm
Cooling Ducts Tk/#: | 4.500 mm / 0.33 | Rad Blds (H,Leg,L): | 15.24/ 15.24/ 19.74 | Lay/Trn/Duc Wts... | : | 2.94/ 0.00/ 0.07
Eff No Cool Ducts.: | HV: 0 Leg: 0 LV: 1 | Axial Allowance...: | 0.000 mm | Total Insul Weight | : | 3.01 kg
Short-Circuit Curr: | 6159 Amp. | Num Support Sticks: | 12
Mean Turn Length..: | 607.171 mm | Lead: Wd / Tk..: | 25.000 / 3.000 mm | Total Coil Weight. | : | 30.87 kg
Max Turn Lth Buckl: | 1510.784 mm | Bus Bar: Wd / Tk..: | 25.000 / 3.000 mm
|  | Layer Insul Tk....: | 0.180 mm
T-RISE/GRADIENT...: | 47.6/22.2 deg C | Watts/sq m .......: | 975.256 | Resistance (Coil). | : | 0.010324 @ 75 C
Turn CSA .........: | 44.400 mm2 |  |  | Conductor Dims.... | : | Specified Size
------------------- | -------------------- | I G H V O L T A | G E W I N D I N G | ------------------ | - | --------------------
Type of Coil......: | Layer-Wound Coil | Coil-Length.......: | 205.000 mm | Cond Mec/Elec Lgth | : | 139.000 / 138.225
Conductor.........: | CU-Round | Inside Dimensions.: | 193.490 x 270.480 | Cond-Dim Per Turn. | : | 1x1x 0.700 x 0.700
Turns Tot./Nominal: | 5401/ 5144 | Outside Dimensions: | 272.182 x 349.172 | Cond Area Per Turn | : | 0.38485 mm2
Cooling Ducts Tk/#: | 4.500 mm / 1.00 | Rad Blds (H,Leg,L): | 39.35/ 39.35/ 39.35 | HV Conductor Wt... | : | 48.97 kg
Eff No Cool Ducts.: | HV: 1 Leg: 1 LV: 1 | Add Rad Allowance.: | 0.000 mm | Lay/Trn/Duc Wts... | : | 7.82/ 0.00/ 0.32
Mean Turn Length..: | 876.5 mm | Layer/Turn Ins Bd.: | 0.400/ 0.075 mm | Insulation Weight. | : | 8.13 kg
LayIns Tk.........: | (29 Full) 0.400 mm | LayIns RB W/OvBld.: | 8.45 mm | Average LayIns Tk. | : | (Strip) 0.265 mm
CURRENT DENSITY...: | 2.625 A/mm2 | # Sup Pts/Ax All..: | 12 / 0.000 mm | Total Coil Weight. | : | 57.10 kg
# Lay: Max/Min tpl: | 31# 178.00/ 61.00 * | Axial Sections....: | 1 | Layer-Layer Volts. | : | 2288.3
T-RISE/GRADIENT...: | 41.3/15.9 deg C | Watts/sq m .......: | 585.971 | Resistance (Coil). | : | 245.6654 @ 75 C
|  |  |  | Conductor Dims.... | : | Standard Size
------------------- | -------------------- | L E C T R I C A L | C L E A R A N C E | ------------------ | - | --------------------
LV to Core Leg(mm): | 1.50x 1.50x 7.00 | LV Cond to Yoke...: | 23.500 mm | Total HV-LV Offset | : | 46.000 mm
Eff Hi-Lo ElecSpan: | 15.000 mm | Ph-Ph Elec Spacing: | 21.000 mm | Max LV Sup Span... | : | 57.000 mm
HV-HSide/HV-LSide.: | 60.00 / 60.00 mm | HV-Ends...........: | 88.000 mm | Yoke-Case Top/Bot. | : | 240.00 / 70.00 mm
HV Fixed Gap......: | 0.000 mm
-------- BASIS FOR | CALCULATIONS ------- | ------------------- | -- MATERIAL PRICES | USD/KG (17-08-01 | ) | -------------------
Netw.Short Cir.Cap: | 1000.0 MVA | E Rnd Wire: AL/CU.: | 12.00 / 22.52 | Core Cost......... | : | 5.02
Wdg Rise Limit....: | 60.0 deg C | Rect Wire : Al/Cu.: | 9.93 / 23.20 | Turn/Lay/DD Insul. | : | 2.18 / 3.28 / 4.1
Top Oil Rise Limit: | 55.0 deg C | Foil Cond: AL/CU..: | 10.85 / 22.56 | Mineral/Silicone.. | : | 1.39 / 6.12
Max No Load/Load..: | 227 / 1560 | LME/1000 (CU/AL)..: | 0 / 0 | Case Steel/Cooling | : | 1.61 / 1.71
------------------- | -------------------- | WEIGHTS, DIMENSIONS | , AND COOLING (RIBS) | ------------------ | - | --------------------
Active Part Weight: | 414 kg |  |  | C&C Dim: Ht/Lgth.. | : | 492.00/ 858.55 mm
Clamp & Brace Wt..: | 41 kg | H-L Barrier Weight: | 4.31 kg
Mineral Oil Weight: | 295 kg | Ribs-Press/Weight.: | 0.16 kp/cm2 79 | Rib Height:1,2,3,4 | : | 600/ 600/ 600/ 600
Bus bar/TC Weight.: | 1/ 0 kg | Rib Pitch: 1,2,3,4: | 85/ 100/ 85/ 100 | No of Ribs:1,2,3,4 | : | 12/ 5/ 12/ 5
Cov/Case & Cooling: | 23/ 106 kg | Rib Depth: 1,2,3,4: | 210/ 50/ 210/ 50 | Rib Pan Wd:1,2,3,4 | : | 1035/ 481/1035/ 481
Total Weight......: | 882 kg | Rib Thick: 1,2,3,4: | 1.20/1.20/1.20/1.20 | Case: Lt/Wd/Ht(mm) | : | 1034.5x 480.7x 802.0
------------------- | -------------------- | ------PRICE & COST | IN USD UNITS ------- | ------------------ | - | --------------------
Core Cost.........: | 1615 | HV / LV Coil Cost.: | 1173/ 641 | Labor & VOH/Hours. | : | 0 / 0
Case/Cooling Cost.: | 43/ 135 | Bracing Cost......: | 67 | Design Matl-Cost.. | : | 4310
Mineral Oil.......: | 411 | Assy and Misc.....: | 225 | Variable Cost..... | : | 4310
EVALUATED LOSSES..: | 0 | EVALUATED COST....: | 4310 | RECOMMENDED PRICE. | : | 8620
------------------- | -------------------- | ---------- PERFORMA | NCE DATA ----------- | ------------------ | - | --------------------
HV Wdg DC Losses..: | 752 Watts | LV Wdg DC Losses..: | 645 Watts
HV Watts (% Eddy).: | 753 ( 0.1) | LV Watts (% Eddy).: | 701 ( 7.6) | LV Bus Bar / Stray | : | 10 / 60
No Load Losses....: | 226 Watts | Tot-Ld Watts(%Ed).: | 1524 ( 8.2) | Total Losses(ONAN) | : | 1750 @ 75 C
% X / % R / % Lead: | 3.99/1.52/0.01 % | % Z (HV-LV-Lead)..: | 4.273 % | TOP OIL RISE...... | : | 31.7 deg C
|  | % Z Guaranteed....: | 4.500 %
------------------- | -------------------- | ------------------- | -------------------- | ------------------ | - | --------------------
TES: HV Axial & Ra | d Factors - 1.000, | 910 LV Rad Fact | or - 0.980 OPT | : (Min Evaluated C | o | st )
MARG/MULT.: < | Rise>: Top Oil= 0 H | 0 L= 0 T= 0 <Loss | >: Core= 1.000 BusB= | 1.0 Eddy H= 1.0 | L | = 1.0 Stray= 1.0
CORE: Std(NO | ) Wds(YES) C-C(NO ) | g(NO ), COND: Foil | Tk(NO ), CLEAR: Wd | O ), CASE: Std(NO |  | ) CALC: Sh Cir(YES)
Circuit Load | Factors: HV= 1.000, | LV= 1.000, TV= 1. | 000
Circuit Load | Factors: HV= 1.000, | LV= 1.000, TV= 1. | 000
Using LTL Cor | e Loss Calculation T | nical Standard: < Y | ES >
Using LTL Loa | d Loss Calculation T | nical Standard: < N | O >
Impedance Mod | el: Convensional
Tapping Turns | @.......: 1 - 5401, | - 5272, 3 - 5144, 4 | - 5015, 5 - 4887

## P
| Section | Value | Row No | Column No
| Start | DESIGN: Data Set 1 | 7 | 2
| Core | C O R E -------- | 10 | 4
| LV | L O W V O L T A | 21 | 3
| HV | I G H V O L T A | 33 | 3
| Clearances | L E C T R I C A L | 44 | 3
| Calculations | CALCULATIONS ------- | 48 | 2
| Weights & Dimensions | WEIGHTS, DIMENSIONS | 15 | 3
| Prices | IN USD UNITS ------- | 58 | 4
| Performance data | NCE DATA ----------- | 62 | 4
| Factors | -------------------- | 67 | 4
Start | 0 | 1 | 2 | 3 | 4 | 5 | 6
-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-1 | TE: 2022.09.15 | 0 | IQUID TYPE TRANSFOR | MER CALCULATION (Ver | n 6.10.0) | 0 | Time: 08:16:38
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | DER : 10033OVL | DESIGN: Data Set 1 | ENGINEER: LASINDU | CUSTOMER NAME | EU | 0 | 0
2 | A - 100 Liquid | Type ONAN Cooli | 60 C Rise Th | ree Phase 50 Hz | Style Number: | 0 | 0
3 | : 33000 + 2- 2x 2. | 50 % TC: Off-load T | Changer | BIL: 170 (Delt | Line/Coil Amps: | 0 | 1.750/ 1.010
4 | : 400 | 0 | 0 | BIL: 3 (Wye | Line/Coil Amps: | 0 | 144.338/ 144.338
5 | ------------------- | -------------------- | ----- S T A C K E D | C O R E -------- | --------- Width -- | 0 | Build ----- Weight -
6 | Core Design.......: | OVAL-IY Mitered | Diagonal Dimension: | 130.000 x 202.490 mm | Step 1: 130.000, | 0 | 72.490 mm 156.8 kg
Core
0 | ------------------- | -------------------- | ----- S T A C K E D | C O R E -------- | --------- Width -- | 0 | Build ----- Weight -
1 | Core Design.......: | OVAL-IY Mitered | Diagonal Dimension: | 130.000 x 202.490 mm | Step 1: 130.000, | 0 | 72.490 mm 156.8 kg
2 | Grade/Frame Type..: | 23ZDKH / 3-Leg | Window Height.....: | 232.000 mm | Step 2: 120.000, | 0 | 50.370 mm 99.2 kg
3 | INDUCTION.........: | 1.450 Tesla | Center to Center..: | 293.182 mm | Step 3: 100.000, | 0 | 32.890 mm 52.5 kg
4 | VPT, W/kg, PBase..: | 6.415, 0.704, 0.53 | Gross/Net CSA.....: | 206.1 / 199.3 cm2 | Step 4: 70.000, | 0 | 26.450 mm 29.6 kg
5 | 100 % Exc Current.: | 0.8241 | Weight of Core-Leg: | 152.1 kg | Step 5: 0.000, | 0 | 0.000 mm 0.0 kg
6 | Sound/Natural Freq: | 44.9 db / 1978 Hz | Weight of Yoke....: | 169.6 kg | Step 6: 0.000, | 0 | 0.000 mm 0.0 kg
7 | Peak HV Inrush Cur: | 13 amp | Core Net Weight...: | 321.7 kg | Step 7: 0.000, | 0 | 0.000 mm 0.0 kg
8 | Utilization Factor: | 0.9080 | Core Scrap Weight.: | 16.4 kg | Step 8: 0.000, | 0 | 0.000 mm 0.0 kg
9 | Standard Core No..: | NONE STANDARD | Core Gross Weight.: | 338.1 kg | Step 9: 0.000, | 0 | 0.000 mm 0.0 kg
10 | Ovality Factor....: | 1.402 | Use Max Steel Wi | dth (Steps minus 1) | Using Std | S | teel Widths
11 | Core Perimeter....: | 553.4 mm | Delta Build.......: | 72.5 mm | 0 | 0 | 0
12 | ------------------- | -------------------- | L O W V O L T A | G E W I N D I N G | ------------------ | - | --------------------
13 | Type of Coil......: | CU-Foil | Coil-Length.......: | 205.000 mm | ELECT LENGTH...... | : | 185.000 mm
14 | TURNS PER COIL....: | 1 x 36.0 | Inside Dimensions.: | 133.000 x205.490 mm | Strip-#x#x Wd x Tk | : | 1x1x 185.00 x 0.240
LV
1 | ------------------- | -------------------- | L O W V O L T A | G E W I N D I N G | ------------------ | - | --------------------
2 | Type of Coil......: | CU-Foil | Coil-Length.......: | 205.000 mm | ELECT LENGTH...... | : | 185.000 mm
3 | TURNS PER COIL....: | 1 x 36.0 | Inside Dimensions.: | 133.000 x205.490 mm | Strip-#x#x Wd x Tk | : | 1x1x 185.00 x 0.240
4 | CURRENT DENSITY...: | 3.251 A/mm2 | Outside Dimensions: | 163.490 x240.480 mm | Cond/Lead Weight.. | : | 26.09 / 1.77 kg
5 | 0 | 0 | Inner Perimeter...: | 562.8 mm | 0 | 0 | 0
6 | Cooling Ducts Tk/#: | 4.500 mm / 0.33 | Rad Blds (H,Leg,L): | 15.24/ 15.24/ 19.74 | Lay/Trn/Duc Wts... | : | 2.94/ 0.00/ 0.07
7 | Eff No Cool Ducts.: | HV: 0 Leg: 0 LV: 1 | Axial Allowance...: | 0.000 mm | Total Insul Weight | : | 3.01 kg
8 | Short-Circuit Curr: | 6159 Amp. | Num Support Sticks: | 12 | 0 | 0 | 0
9 | Mean Turn Length..: | 607.171 mm | Lead: Wd / Tk..: | 25.000 / 3.000 mm | Total Coil Weight. | : | 30.87 kg
10 | Max Turn Lth Buckl: | 1510.784 mm | Bus Bar: Wd / Tk..: | 25.000 / 3.000 mm | 0 | 0 | 0
11 | 0 | 0 | Layer Insul Tk....: | 0.180 mm | 0 | 0 | 0
12 | T-RISE/GRADIENT...: | 47.6/22.2 deg C | Watts/sq m .......: | 975.256 | Resistance (Coil). | : | 0.010324 @ 75 C
13 | Turn CSA .........: | 44.400 mm2 | 0 | 0 | Conductor Dims.... | : | Specified Size
HV
2 | ------------------- | -------------------- | I G H V O L T A | G E W I N D I N G | ------------------ | - | --------------------
3 | Type of Coil......: | Layer-Wound Coil | Coil-Length.......: | 205.000 mm | Cond Mec/Elec Lgth | : | 139.000 / 138.225
4 | Conductor.........: | CU-Round | Inside Dimensions.: | 193.490 x 270.480 | Cond-Dim Per Turn. | : | 1x1x 0.700 x 0.700
5 | Turns Tot./Nominal: | 5401/ 5144 | Outside Dimensions: | 272.182 x 349.172 | Cond Area Per Turn | : | 0.38485 mm2
6 | Cooling Ducts Tk/#: | 4.500 mm / 1.00 | Rad Blds (H,Leg,L): | 39.35/ 39.35/ 39.35 | HV Conductor Wt... | : | 48.97 kg
7 | Eff No Cool Ducts.: | HV: 1 Leg: 1 LV: 1 | Add Rad Allowance.: | 0.000 mm | Lay/Trn/Duc Wts... | : | 7.82/ 0.00/ 0.32
8 | Mean Turn Length..: | 876.5 mm | Layer/Turn Ins Bd.: | 0.400/ 0.075 mm | Insulation Weight. | : | 8.13 kg
9 | LayIns Tk.........: | (29 Full) 0.400 mm | LayIns RB W/OvBld.: | 8.45 mm | Average LayIns Tk. | : | (Strip) 0.265 mm
10 | CURRENT DENSITY...: | 2.625 A/mm2 | # Sup Pts/Ax All..: | 12 / 0.000 mm | Total Coil Weight. | : | 57.10 kg
11 | # Lay: Max/Min tpl: | 31# 178.00/ 61.00 * | Axial Sections....: | 1 | Layer-Layer Volts. | : | 2288.3
12 | T-RISE/GRADIENT...: | 41.3/15.9 deg C | Watts/sq m .......: | 585.971 | Resistance (Coil). | : | 245.6654 @ 75 C
13 | 0 | 0 | 0 | 0 | Conductor Dims.... | : | Standard Size
14 | ------------------- | -------------------- | L E C T R I C A L | C L E A R A N C E | ------------------ | - | --------------------
Clearances
3 | ------------------- | -------------------- | L E C T R I C A L | C L E A R A N C E | ------------------ | - | --------------------
4 | LV to Core Leg(mm): | 1.50x 1.50x 7.00 | LV Cond to Yoke...: | 23.500 mm | Total HV-LV Offset | : | 46.000 mm
5 | Eff Hi-Lo ElecSpan: | 15.000 mm | Ph-Ph Elec Spacing: | 21.000 mm | Max LV Sup Span... | : | 57.000 mm
6 | HV-HSide/HV-LSide.: | 60.00 / 60.00 mm | HV-Ends...........: | 88.000 mm | Yoke-Case Top/Bot. | : | 240.00 / 70.00 mm
7 | HV Fixed Gap......: | 0.000 mm | 0 | 0 | 0 | 0 | 0
8 | -------- BASIS FOR | CALCULATIONS ------- | ------------------- | -- MATERIAL PRICES | USD/KG (17-08-01 | ) | -------------------
9 | Netw.Short Cir.Cap: | 1000.0 MVA | E Rnd Wire: AL/CU.: | 12.00 / 22.52 | Core Cost......... | : | 5.02
10 | Wdg Rise Limit....: | 60.0 deg C | Rect Wire : Al/Cu.: | 9.93 / 23.20 | Turn/Lay/DD Insul. | : | 2.18 / 3.28 / 4.1
Calculations
4 | -------- BASIS FOR | CALCULATIONS ------- | ------------------- | -- MATERIAL PRICES | USD/KG (17-08-01 | ) | -------------------
5 | Netw.Short Cir.Cap: | 1000.0 MVA | E Rnd Wire: AL/CU.: | 12.00 / 22.52 | Core Cost......... | : | 5.02
6 | Wdg Rise Limit....: | 60.0 deg C | Rect Wire : Al/Cu.: | 9.93 / 23.20 | Turn/Lay/DD Insul. | : | 2.18 / 3.28 / 4.1
7 | Top Oil Rise Limit: | 55.0 deg C | Foil Cond: AL/CU..: | 10.85 / 22.56 | Mineral/Silicone.. | : | 1.39 / 6.12
8 | Max No Load/Load..: | 227 / 1560 | LME/1000 (CU/AL)..: | 0 / 0 | Case Steel/Cooling | : | 1.61 / 1.71
9 | ------------------- | -------------------- | WEIGHTS, DIMENSIONS | , AND COOLING (RIBS) | ------------------ | - | --------------------
10 | Active Part Weight: | 414 kg | 0 | 0 | C&C Dim: Ht/Lgth.. | : | 492.00/ 858.55 mm
11 | Clamp & Brace Wt..: | 41 kg | H-L Barrier Weight: | 4.31 kg | 0 | 0 | 0
Weights & Dimensions
-1 | ------------------- | -------------------- | WEIGHTS, DIMENSIONS | , AND COOLING (RIBS) | ------------------ | - | --------------------
0 | Active Part Weight: | 414 kg | 0 | 0 | C&C Dim: Ht/Lgth.. | : | 492.00/ 858.55 mm
1 | Clamp & Brace Wt..: | 41 kg | H-L Barrier Weight: | 4.31 kg | 0 | 0 | 0
2 | Mineral Oil Weight: | 295 kg | Ribs-Press/Weight.: | 0.16 kp/cm2 79 | Rib Height:1,2,3,4 | : | 600/ 600/ 600/ 600
3 | Bus bar/TC Weight.: | 1/ 0 kg | Rib Pitch: 1,2,3,4: | 85/ 100/ 85/ 100 | No of Ribs:1,2,3,4 | : | 12/ 5/ 12/ 5
4 | Cov/Case & Cooling: | 23/ 106 kg | Rib Depth: 1,2,3,4: | 210/ 50/ 210/ 50 | Rib Pan Wd:1,2,3,4 | : | 1035/ 481/1035/ 481
5 | Total Weight......: | 882 kg | Rib Thick: 1,2,3,4: | 1.20/1.20/1.20/1.20 | Case: Lt/Wd/Ht(mm) | : | 1034.5x 480.7x 802.0
6 | ------------------- | -------------------- | ------PRICE & COST | IN USD UNITS ------- | ------------------ | - | --------------------
7 | Core Cost.........: | 1615 | HV / LV Coil Cost.: | 1173/ 641 | Labor & VOH/Hours. | : | 0 / 0
8 | Case/Cooling Cost.: | 43/ 135 | Bracing Cost......: | 67 | Design Matl-Cost.. | : | 4310
Prices
6 | ------------------- | -------------------- | ------PRICE & COST | IN USD UNITS ------- | ------------------ | - | --------------------
7 | Core Cost.........: | 1615 | HV / LV Coil Cost.: | 1173/ 641 | Labor & VOH/Hours. | : | 0 / 0
8 | Case/Cooling Cost.: | 43/ 135 | Bracing Cost......: | 67 | Design Matl-Cost.. | : | 4310
9 | Mineral Oil.......: | 411 | Assy and Misc.....: | 225 | Variable Cost..... | : | 4310
10 | EVALUATED LOSSES..: | 0 | EVALUATED COST....: | 4310 | RECOMMENDED PRICE. | : | 8620
11 | ------------------- | -------------------- | ---------- PERFORMA | NCE DATA ----------- | ------------------ | - | --------------------
12 | HV Wdg DC Losses..: | 752 Watts | LV Wdg DC Losses..: | 645 Watts | 0 | 0 | 0
13 | HV Watts (% Eddy).: | 753 ( 0.1) | LV Watts (% Eddy).: | 701 ( 7.6) | LV Bus Bar / Stray | : | 10 / 60
Performance data
7 | ------------------- | -------------------- | ---------- PERFORMA | NCE DATA ----------- | ------------------ | - | --------------------
8 | HV Wdg DC Losses..: | 752 Watts | LV Wdg DC Losses..: | 645 Watts | 0 | 0 | 0
9 | HV Watts (% Eddy).: | 753 ( 0.1) | LV Watts (% Eddy).: | 701 ( 7.6) | LV Bus Bar / Stray | : | 10 / 60
10 | No Load Losses....: | 226 Watts | Tot-Ld Watts(%Ed).: | 1524 ( 8.2) | Total Losses(ONAN) | : | 1750 @ 75 C
11 | % X / % R / % Lead: | 3.99/1.52/0.01 % | % Z (HV-LV-Lead)..: | 4.273 % | TOP OIL RISE...... | : | 31.7 deg C
12 | 0 | 0 | % Z Guaranteed....: | 4.500 % | 0 | 0 | 0
13 | ------------------- | -------------------- | ------------------- | -------------------- | ------------------ | - | --------------------
Factors
8 | ------------------- | -------------------- | ------------------- | -------------------- | ------------------ | - | --------------------
9 | TES: HV Axial & Ra | d Factors - 1.000, | 910 LV Rad Fact | or - 0.980 OPT | : (Min Evaluated C | o | st )
10 | MARG/MULT.: < | Rise>: Top Oil= 0 H | 0 L= 0 T= 0 <Loss | >: Core= 1.000 BusB= | 1.0 Eddy H= 1.0 | L | = 1.0 Stray= 1.0
11 | CORE: Std(NO | ) Wds(YES) C-C(NO ) | g(NO ), COND: Foil | Tk(NO ), CLEAR: Wd | O ), CASE: Std(NO | 0 | ) CALC: Sh Cir(YES)
12 | Circuit Load | Factors: HV= 1.000, | LV= 1.000, TV= 1. | 000 | 0 | 0 | 0
13 | Circuit Load | Factors: HV= 1.000, | LV= 1.000, TV= 1. | 000 | 0 | 0 | 0
14 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | Using LTL Cor | e Loss Calculation T | nical Standard: < Y | ES > | 0 | 0 | 0
16 | Using LTL Loa | d Loss Calculation T | nical Standard: < N | O > | 0 | 0 | 0
17 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Q
MARGINS
Core Loss | 10
Cu Loss | 10
No Load Current | 30
Total Weight | 100
Material Name in MM | Margin (%)
Fin Radiators | 0 | 0 |  | 2.5
| 0 | 0 |  | 2.5
Panel Type Radiators | 0 | 0 |  | 2.5 |  |  | Removable
Cover+Base+Flange | 0 | 0 |  | 2.5
Steel (Total) | 0 | 0 |  | 2.5
Wooden Total | 0 | 0 |  | 2.5
Core steel | 0 | 0 |  | 2.5
Oil | 0 | 0 |  | 2.5
Copper Foil | 0 | 0 |  | 2.5
Round Copper | 0 | 0 |  | 2.5
Copper Bus Bar | 0 | 0 |  | 2.5
Rectangular Copper | 0 | 0 |  | 2.5
DDP-Double Layer | 0 | 0 |  | 2.5
0.15 DDP-Single Layer | 0 | 0 |  | 2.5
0.25 DDP-Single Layer | 0 | 0 |  | 2.5
Strip Insulation | 0 | 0 |  | 2.5
Corrugator Boards- 9.0x2.0 mm | 0 | 0 |  | 2.5
LV Strip | 0 | 0 |  | 2.5
HV Strip | 0 | 0 |  | 2.5
Galvanizing | 0 | 0 |  | 2.5
Primer Paint & Thinner | 0 | 0 |  | 2.5
Powder Paint | 0 | 0 |  | 2.5
Rectangular Copper
ELECTRICAL DATA
TYPE | Fin Radiator |  |  | Ribs | Ribs-Press/Weight.:
| Hermetically Sealed |  |  | 0 | 0
| N | N
Hermetically Sealed
Conservator Type
Fin Radiator
Panel type
Y
N
kVA | 100 | 3 | 13 |  |  |  |  | Tap Wire | Area | Ph density | Line Density | ph (kg) | line (kg)
HV VOLTS | 33000 | 1 | 9 | 18 |  |  |  | 3 | 7.0686 | 0.14289 | 0.24757 | 3 | 1
LV VOLTS | 400 | 1 | 7 |  |  |  |  | 7/1.7 | 15.8886 | 0.063568 | 0.11014 | 0 | 0
LV Coil current | 144.338 | 8 | 16 | 144.338/ 144.338 |  | 1 | 2 | 19/1.35 | 27.1964 | 0.037137 | 0.064347 | 0 | 0
LV line current | 144.338 | [6 empty] | Choise |  | 0.14289 | 0.24757
LV Coil current density | 3.251 | 7
: 33000 + 2- 2x 2. | [7 empty] | Capacity | Tapping | Barrier DDP
HV coil current | 1.01 | 12 | 7 | 1.750/ 1.010 |  | Closest capacity | 100 | 100 | 3 | 0.5
HV line current | 1.75 |  |  |  |  | Tapping Weight | 3 | 160 | 3 | 0.5
[8 empty] | 250 | 4 | 0.75
HV voltage (kV) | 33 | [6 empty] | 400 | 4 | 1
Basic Insulation Level | 170 | 4 | 10 |  |  |  |  | 630 | 5 | 1.5
%X | 3.99 | 16 | 10 | 5 | 3.99/1.52/0.01 % | % X / % R / % Lead: |  | 800 | 5 | 2
%R | 1.52 | [6 empty] | 1000 | 6 | 2.5
Frequency | 50 | 5 | 18 |  |  |  |  | 1250 | 6 | 3.5
Phases | 3 | ree | [5 empty] | 1600 | 7 | 4.5
Tappings |  | 9 | 12 | 18 |  |  |  | 2000 | 7 | 5.5
+ | 2 | [6 empty] | 2500 | 8 | 6.5
- | -2 | 2 | [5 empty] | 3150 | 13 | 7.5
Steps | 2.5 | 4 | 5
| 5% | 2 | 1
| 2.5% | 1 | 2
| 0% | 0 | 3
| -2.5% | -1 | 4
| -5% | -2 | 5
| - | 0
| - | 0
| - | 0
| - | 0
Vector Group
LV | yn |  | yn
HV | D |  | D
Dyn
Dyn11
Temp. Rise Windings | 60 | 12 | 60
Temp. Rise Top oil | 55 | 11 | 55
% impedence | 4.78 | 4.273 % | % Z (HV-LV-Lead)..: |  | 4.273 | 4.273
Full Load Loss | 1560 | 1.1 | 701 |  |  | 1560
No Load Loss | 227 | 1.1 | #VALUE! | #VALUE! |  | 227 |  |  | 4.2151 | 0.701
No load Current | 0.8241
Sound level | 45
Core Loss Factor | 1 | 16 | 8
Factor k x sqrt(2) | #VALUE! | #VALUE! | #VALUE!
kVA | % Z | % Z-pu | FL loss | NL loss | PU load | PF | X | sin X | %X | %R | %FE | %Eff | %Reg
100 | 4.78 | 4.78 | 1560 | 227 | 1 | 0.8 | 0.6435 | 0.6 | 4.5183 | 1.56 | 0.227 | 97.8151 | 3.9948
DIMENSIONS
CASE
Case-Length | 1035 | 14 | 7 | 20
Case-Width | 481
Case-Height | 802
HEIGHTS |  | WEIGHTS
Conservator | 0 | 0
HV Box | 0 | 0
ISD | 0 | 0
Plug-in Type 36 kV 250 A Interface B | 150 | 15
EN 250 | 120 | 1.72
LV Box | 0 | 0
Height for base skid and cover | 90 | 22.0516
CABLE BOX
No of intakes /Phase (LV) | 4
LV Box Depth | 0 |  |  | Conservator Length | 0
LV Box Width | 0 |  |  | Panel Add. to Length | 0
HV Box Depth | 0 |  |  | Panel Add. to Width | 0
HV Box Width | 0
WTI Box Depth | 400
Tolerance
Length | 1555 | 20 | 1535
Width | 921 | 20 | 901
Height | 1062 | 20 | 1042
Weight-TOTAL | 980 | 50 | 921
Weight-OIL | 300 |  | 300
Weight-ACTIVE PART | 420 |  | 414
Weight-Untanking | 490 | 50 | 434
Container Arrangement |  | 40' |  |  | 20'
Length |  | 12045 |  |  | 5919
Width |  | 2280 |  |  | 2286
Weight | 100 | 27396 |  |  | 22100
Length/Length |  | 7 | 2 |  | 3 | 2
Length/Width |  | 13 | 1 |  | 6 | 1
Weight | 14 | 25 |  | 6 | 20
DESIGN
Design | 10033OVL |  |  | DER : 10033OVL
Date | 2022.09.15 | 5 | 6 | Time: 08:16:38 | IQUID TYPE TRANSFOR |  |  | TE: 2022.09.15
Time | 08:16:38 | [6 empty] | 3
Customer | EU
WINDING DATA
Coil Length | 205 | 203 | 139 | 138.225 | 185 | 0 | 1
Window height | 232 | 232.000 | 9
Center to center | 294 | 293.182 | 9
Core Type | OVAL-IY
Height from yoke to cover | 240 | 70.00 mm | 70
LV layer insulations thickness | 0.18
INSULATION
LV layer insulations thickness | 0.15 | 0.18 | 2.94 | 25.000 | 0.180
203mm x 0.15 DDP DL | 2.94 | 1 |  |  |  | 0.15 DDP | 0.25 DDP | 0.15 DDP | 0.25 DDP
203mm x 0.15 DDP SL | 0 | 0 |  |  | 0.15 | 1 |  | 1
203mm x 0.25 DDP SL | 0 | 0 |  |  | 0.18 | 1 |  | 1
[5 empty] | 0.25 | 1 |  | 1
[5 empty] | 0.3 | 1 |  | 2
HV layer insulations thickness | 0.4 | 0.4 | 7.82 |  | 0.35 |  | 1 |  | 1
203mm x 0.15 DDP SL | 0 | 0 |  | 0.4 | 0.4 | 0.5 | 0.5 | 1 | 1
203mm x 0.25 DDP SL | 0.5 | 0 |  | 0.265 | 0.45 | 1 |  | 3
[5 empty] | 0.5 |  | 1 |  | 2
HV strip insulations thickness |  |  | 7.82 |  | 0.55 | 0.67 | 0.33 | 2 | 1
33 x 0.05 mm Strip | 11.0587 | 1 |  |  | 0.6 | 1 |  | 4
33 x 0.075 mm Strip | 0 | 0 |  |  | 0.65 |  | 1 |  | 2
[5 empty] | 0.7 | 0.75 | 0.25 | 3 | 1
203mm x 0.15 DDP DL | 2.94 |  |  |  | 0.75 |  | 1 |  | 3
203mm x 0.15 DDP SL | 0 |  |  |  | 0.8 | 0.5 | 0.5 | 2 | 2
203mm x 0.25 DDP SL | 0.5 |  |  |  | 0.85 | 0.8 | 0.2 | 4 | 1 | Edge Strips
[5 empty] | 0.9 | 0.25 | 0.75 | 1 | 3 | 8
LV edge strip | 8 |  |  |  | 0.95 |  | 1 |  | 3 | 18
20 | 0.2 | 13 | 19 |  | 1.00 |  | 1 |  | 4 | 27
607.171 | 36.0 | 3 | 10 | 3 | 1.1 | 0.66667 | 0.33333 | 4 | 2 | 33
| #VALUE! |  |  |  | 1.2 | 1 |  | 8 | 0 | 45
21858.156 | 0.22558 |  |  |  | 1.25 |  | 1 | 0 | 4
8 | 0.25 |  |  |  | 1.3 | 0.67 | 0.33 | 4 | 2
HV edge strip | 33 |  |  |  | 1.4 | 0.75 | 0.25 | 6 | 2
66 | 0.700 | 12 | 18 |  | 1.5 |  | 1 |  | 6
876.5 | 31 |  |  |  | 1.6 | 0.5 | 0.5 | 4 | 4
27171.5 | 3.2387 |  |  |  | 1.7 | 0.8 | 0.2 | 8 | 2
33 | 0.25 |  |  |  | 1.8 | 0.25 | 0.75 | 2 | 6
Duct Space |  |  |  |  | 1.9 |  | 1 |  | 6
LV | 0.07 | 18 | 12 | 5 | 2 |  | 1 |  | 8
HV | 0.32 | 18 | 12 | 5 | 2.1 | 0.4 | 0.6 |  | 8
| 0.39 |  |  |  | 2.2 | 0.66667 | 0.33333 | 1 | 8
Corragated Board |  |  |  |  | 2.3 | 0.17 | 0.83 | 2 | 10
| 4.31 | 6 |  |  | 2.45 | 0.23 | 0.77 | 3 | 10
CORE STEEL
Core Steel | Builds(mm) | Weight(kg) | : | . | "(10)" | "m" | *100 | "k" | Weight | Adjusted Build
130 | 73 | 156.8 | 7 | 13 | 73 | 8 | 0 | 19 | 156.8 | #VALUE! |  | 130
120 | 51 | 99.2 | 7 | 13 | 51 | 8 | 0 | 19 | 99.2 | 51 |  | 120 | #VALUE! | #VALUE!
100 | 33 | 52.5 | 7 | 13 | 33 | 8 | 0 | 19 | 52.5 | 33 |  | 100 | #VALUE!
70 | 27 | 29.6 | 7 | 13 | 27 | 8 | 0 | 19 | 29.6 | #VALUE! |  | 70 | #VALUE!
0 | 0 | 0 | 7 | 13 | 0 | 7 | 0 | 18 | 0.0 | 0
0 | 0 | 0 | 7 | 13 | 0 | 7 | 0 | 18 | 0.0 | 0 |  |  | 70
0 | 0 | 0 | 7 | 13 | 0 | 7 | 0 | 18 | 0.0 | 0
0 | 0 | 0 | 7 | 13 | 0 | 7 | 0 | 18 | 0.0 | 0
0 | 0 | 0 | 7 | 13 | 0 | 7 | 0 | 18 | 0.0 | 0
TOTAL | 184 | 338.1 | 338.1
core steel type | 23ZDKH
core steel thickness | 23ZDKH85
COPPER
LV | CU-foil
AL-foil
CU-layer-rect
HV | CU-round
CU-rectangular
LV Cu
CU-Foil | 185.00 x 0.24 | 19 | 4 | 2
CU-Foil | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| 185.00 x 0.24 | 185 | 0.24
185.00 x 0.24mm CU-Foil | 26.09 | 26.09
HV Cu
CU-Round | 0.700 x 0.700 | 18 | 12 | 4 | 2 | 1
0.700
0.700mm CU-Round | 48.97 | 48.97
Flat Cu
LV Leads | 1.77 | 7 | 16
Bus Bars | 1
Total | 2.77 |  | 3 | 25 | 17 | 8 | 18
3*25mm | 4.1498
Inhibited Mineral Oil | 339.0805
STEEL
Steel Density (kg/mm3) | 7.85e-06
Steel Weights | From Program | Calculated
Cover | 23 | 20.2999 | 3 | 11
Case + Cooling | 106
Case | 27 | 44.2738
Clamps | 41 | 29.1219 | 4
Conservator | 0 | 0 | #VALUE!
| 91 | 94
94
Radiator Weights
Fin Type Radiators | 79 | 14 | 10
Panel Type Radiators | 0 | 6
79
79
Galvanize | 129
Steel Channel
MS Ch 76x38x6 , L= 1025mm | 840
MS Ch 100x50x6 , L= 1025mm | 1128
MS Ch 127x64x6 , L= 1025mm | 1458
MS Ch 152x76x6 , L= 1025mm | 1752
MS Ch 200x75x9 , L= 1025mm | 2988
4mm MS Plate 1025x192x4mm | 768
Base Skid
50x50x6 AI | 50 | 564
76x38x6 MS Channel | 76 | 840 |  | 400 upto including
100x50x6 MS Channel | 100 | 1128 |  | 1000 upto inc
152x152x10 H Iron | 152 | 4360 |  | 2500
250x75x9 MS Channel | 200 | 2988 |  | >2500
| Dimensions |  |  | MS Plate Arrangement-I |  |  | MS Plate Arrangement-II |  |  |  |  | WEIGHT
MS Sheet -Length | 2440
MS Sheet -Width | 1220
| Thickness | Width | Length | L/L | W/W | Nos | L/W | W/L | Nos | Nos of transformer | Required Nos
Cover plate | 4 | 541 | 1195 | 2 | 2 | 4 | 4 | 1 | 4 | 4 | 19 | 20.2999
Base | 3 | 1135 | 825 | 2 | 1 | 2 | 2 | 1 | 2 | 2 | 37 | 22.0516
Conservator | 3 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 0
Nos of Sheets
Tank | 6 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
| Thickness | Width | Length | Description | Qty | CSA | WEIGHT
Stay rod | 10 | - | 548 | 10mm BS Rod | 0 | 79
Tie Rod | 10 | - | 274 | 10mm BS Rod | 4 | 79
Flange Long side | 6 | 50 | 1135 | 50x50x6 Angle Iron | 2 | 564 | 10.0502
Flange Short side | 6 | 50 | 481 | 50x50x6 Angle Iron | 2 | 564 | 4.2592 |  |  |  | cons
Traverse-Horizontal | 6 | 75 | 184 | 75x6 Flat Iron | 0 | 450 | 0
Traverse-Vertical | 6 | 75 | 290 | 75x6 Flat Iron | 0 | 450 | 0
Foot | 10 | 75 | 374 | 75x10 Flat Iron | 2 | 750 | 4.4038
Base Skid | - | 76 | 600 | 76x38x6 MS Channel | 2 | 840 | 7.9128
Steel Channel | 4 | 192 | 1025 | 4 mm MS Plate | 4 | 768 | 24.7181
Wooden cross cut height | 10 | 50 | 750 | 0 | 0 | 500
Wooden clamp height | 110 | 25 | 1015 | 0 | 0 | 2750
COOLING
Panel Radiators | NO | 12
600/ 600/ 600/ 600 | 5 | 10 | 0
No of radiators | 0
Elements/radiator | 600/
Center to center distance | 0
Depth of a radiator | #VALUE!
Width of radiator flange | 150
Radiator width | 520
Distance bet 2 radiators | 80
Offset for off-central type | 131
PANEL TYPE RADS | LV | HV | Cons. Side | Other Side | Length Addition | Width Addition
1 | 1 | 0 | 0 | 0 | 0 | #VALUE!
1 | 2 | 0 | 0 | 0 | 0 | #VALUE!
3 | 2 | 1 | 0 | 0 | 0 | #VALUE!
4 | 2 | 2 | 0 | 0 | 0 | #VALUE!
5 | 2 | 2 | 1 | 0 | #VALUE! | #VALUE!
6 | 2 | 2 | 2 | 0 | #VALUE! | #VALUE!
7 | 2 | 2 | 2 | 1 | #VALUE! | #VALUE!
8 | 2 | 2 | 2 | 2 | #VALUE! | #VALUE!
Fin depth-long side | 210 | 9 | 4
Fin depth-short side | 50
Fin height | 600 | 4
Fin Thickness | 600 | 1.2 | 1.2 | 10 | 5
Labour Hours |  |  | 0 | #REF!
| 10 |  |  | 0
| 10 |  |  | 0
#REF!
ACCESSORIES
HV Bushings | Plug-in Type 36 kV 250 A Interface B |  |  | 150 | 3 | 5 | 3
170 | 36 | 170 | 250 |  |  |  | 4
Selection | Voltage (kV) | BIL (kV) | Current (A) | Height (mm) | Description | Weight (kg)
0 | 12 | 75 | 250 | 310 | 10 NF 250 CD = 305 mm | 5.65
0 | 12 | 75 | 630 | 342 | 10 NF 630 | 8
0 | 12 | 75 | 250 | 150 | 1M (B9722) | 5
0 | 24 | 125 | 250 | 310 | 24 NF 250 P3 CD = 605 mm | 5.65
0 | 24 | 125 | 250 | 150 | Plug-in Type 24 kV 250 A Interface B | 5
0 | 24 | 125 | 630 | 150 | Plug-in Type 24 kV 630 A Interface C | 6.5
0 | 36 | 200 | 250 | 520 | 30 NF 250 CD = 900 mm | 9.35
0 | 36 | 200 | 250 | 520 | 30 NF 250 CD = 1116 mm | 12.55
0 | 36 | 200 | 250 | 520 | 30 NF 250 CD = 1920 mm | 12.55
1 | 36 | 170 | 250 | 150 | Plug-in Type 36 kV 250 A Interface B | 5
0 | 36 | 170 | 630 | 150 | Plug-in Type 36 kV 630 A Interface C | 6.5
0 | 52 | 250 | 1000 | 150 | Plug-in Type 52 kV 1000 A Interface F | 8
0 | 42 | 200 | 250 | 500 | 40 NF 250 | 15
0 | 52 | 250 | 1000 | 730 | 52 NF 1000 CD = 1430 mm | 35.2
LV Bushings | EN 250 |  | 120 | 0.43 | 4 |  | 3
144.338 | 1 | 250 |  |  |  |  | 4
Selection | Voltage (kV) | Current (A) | Height (mm) | Weight (kg) | Description |  | 6
8
1 | 1 | 250 | 120 | 0.43 | EN 250 | 250
0 | 1 | 630 | 165 | 1.16 | EN 630 | 630
0 | 1 | 1250 | 177 | 2.73 | EN 1250 | 1250
0 | 1 | 2000 | 240 | 6.24 | EN 2000 | 2000
0 | 1 | 2500 | 177 | 2.73 | EN 1250 | 1250
0 | 1 | 3150 | 250 | 8.45 | EN 3150 | 3150
0 | 1 | 4000 | 240 | 6.24 | EN 2000 | 2000
0 | 1 | 6300 | 250 | 8.45 | EN 3150 | 3150
0 | 12 | 250 | 310 | 5.65 | 10 NF 250 | 250
0 | 12 | 630 | 310 | 8 | 10 NF 630 | 630
0 | 12 | 250 | 150 | 5 | 1M (B9722) | 250
0 | 24 | 250 | 150 | 5 | Plug-in Type 24 kV 250 A Interface B | 250
0 | 24 | 630 | 150 | 6.5 | Plug-in Type 24 kV 630 A Interface C | 630
Tap selector | HR 7A3.335 (30kV 30A 100mm 5 Pos) | [5 empty] | 0
0 | 30 | 30 | 200 | 5 |  |  | 1
Selection | Voltage (kV) | Current (A) | BIL (kV) | Positions | Description
0 | 20 | 30 | 95 | 5 | HR 7A3.235 (20kV 30A 100mm 5 Pos)
0 | 20 | 30 | 95 | 7 | HR 7A3.235 (20kV 30A 100mm 7 Pos)
0 | 20 | 63 | 95 | 5 | HM 25.43.885 (20kV 63A 131mm 5 Pos)
0 | 20 | 120 | 95 | 5 | HM 28.43.885 (20kV 120A 131mm 5 Pos)
0 | 20 | 250 | 95 | 5 | HM 28.43.885 (20kV 250A 131mm 5 Pos)
1 | 30 | 30 | 200 | 5 | HR 7A3.335 (30kV 30A 100mm 5 Pos)
0 | 30 | 30 | 200 | 7 | HR 7A3.335 (30kV 30A 100mm 7 Pos)
0 | 30 | 30 | 200 | 5 | HM 23.44.885 (30kV 30A 131mm 5 Pos)
0 | 30 | 30 | 200 | 7 | HM 23.44.885 (30kV 30A 131mm 7 Pos)
0 | 30 | 63 | 200 | 5 | HM 25.44.885 (30kV 63A 131mm 5 Pos)
Valves
PRV T-10K1 1R"
PRV T-50 0.4 BAR
DRAIN VALVE NW 22
AIR RELEASE PLUG
ARES DIN25 DOUBLE FLANGE GATE VALVE
SINGLE FLANGE BALL VALVE 1" NW25S-SS
THROTTLE VALVE FOR RADIATOR NW80 FORMB
BALL VALVE 1" PELGER
GATE VALVE WITH SAMPLING
GATE VALVE WITHOUT SAMPLING
SAMPLING VALVE
BALL VALVE 1" Threaded on both sides
Oil Level Indicators
Magnetic- with 400mm boss
Magnetic- with 200mm boss
4 HOLES PRISMATIC
6 HOLES PRISMATIC
8 HOLES PRISMATIC
FLOATING TYPE
VIAT SO4 - Dial Type with Contacts
VIAT SO6 - Dial Type with Contacts
Cable Boxes | [5 empty] | HV Cable Boxes | Selection | Price | Depth | Width | H above cover | Weight
HV CABLE BOX | 0 |  |  |  |  | Plug-In Cable Box | 0 | 350 | 1052 | 747 | 391 | 100
LV CABLE BOX | 0 |  |  |  |  | 1M Cable Box | 0 | 350 | 862 | 578 | 318 | 57
WTI BOX | 0
CONNECTOR BOX | 0 |  |  |  |  | LV Cable Boxes |  | Price | Depth | Width | H above cover | Weight
HV ENCLOSURE | 0 |  |  |  |  | EN 250 | 0 | 500 | 933 | 770 | 331 | 85
Other Parts | [5 empty] | EN 630 | 0 | 600 | 933 | 770 | 331 | 135
RATING PLATE | [5 empty] | EN 1250 | 0 | 700 | 1085 | 1073 | 386 | 150
PHASE MARKING PLATES | [5 empty] | EN 1250 x 2 | 0 | 750 | 1085 | 1073 | 386 | 180
S/A MOUNTING BRACKET A-2 | [5 empty] | EN 2000 | 0 | 800 | 1065 | 1115 | 431 | 200
ISD UNIT | [5 empty] | EN 2000 x 2 | 0 | 850 | 1420 | 1115 | 431 | 230
BREATHER 1KG TYPE A | [5 empty] | EN 3150 | 0 | 900 | 1140 | 1185 | 518 | 300
BREATHER 1KG TYPE B | [5 empty] | EN 3150 x 2 | 0 | 950 | 1495 | 1133 | 518 | 340
BREATHER 1KG TYPE C
BREATHER 2KG | [5 empty] | WTI Box | 0 | 250 | 400 | 700 | 500 | 10
THERMOMETER TEK 16 | [5 empty] | Connector Box | 0 | 150 | 300 | 500 | 300 | 5
THERMOWELL 3/4" BSP | [5 empty] | HV Enclosure | 0 | 250 | 630 | 750 | 400 | 15
THERMOMETER POCKET
GALVANIZED CUP FOR THERMOMETER POCKET
BUCHOLZ RELAY EW712
CONSERVATOR FILLING CAP AL. 2"
T/F WHEEL 7613T00691 |  |  |  | SDF |  | HRC Fuse
T/F WHEEL 7613T00691 |  |  |  | Current | 200 | 160
OIL TEMP. INDICATOR TD50 (354 01 12X6.0) |  |  |  | 20 | 20A 3KL81113HA10
WINDING TEMP. INDICATOR TD76 (354 01 12X6.0) |  |  |  | 32 | 32A 3KL81213HA10
RTD WTI (PT100) |  |  |  | 63 | 63A 3KL81513HA10
RTD OTI (PT100) |  |  |  | 100 | 100A 3KL82113HA10
CT 3000/2A Oil Immersed (Measuring) Ring Type 15VA/0.5 |  |  |  | 125 | 125A 3KL82213HA10
CT 5000/5A Oil Immersed (Measuring) Ring Type 15VA/0.5 |  |  |  | 160 | 160A 3KL82313HA10
CT 1600/1A 5P20 15VA/0.5 2 Core |  |  |  | 200 | 200A 3KL83113HA10
NCT 400/1A 5P20 15VA |  |  |  | 250 | 250A 3KL83213HA10
NCT 1600/1A 5P20 15VA |  |  |  | 315 | 315A 3KL83313HA10
NCT 2000/1A 5P20 15VA |  |  |  | 400 | 400A 3KL83413HA10
CT TERMINAL BOX (2 TERMINALS) |  |  |  | 500 | 500A 3KL84113HA10
CT TERMINAL BOX (4 TERMINALS) |  |  |  | 630 | 630A 3KL84213HA10
CT TERMINAL BOX (6 TERMINALS) |  |  |  | 800 | 800A 3KL84313HA10
24kV ELBOW CONNECTOR SET (03)
36kV ELBOW CONNECTOR SET (03)
52kV ELBOW CONNECTOR SET (04)
OBO SURGE ARRESTERS
LTL Name Board
Nut, Bolt & 2 Washers (Galvanized) M10 x 40 mm
Split washers for tank cover fixing
M12 bolt, nut, spring washer & lock washer for earthing terminal
Flange Gasket
Wooden Pallete For Packing
Painting |  |  |  |  | Capacity | 2 Coat Sys - DFT 130 |  | 3 Coat Sys - DFT 250
GALVANIZING |  |  | 0 |  | 250 | Primer (kg) | Powder (kg) | Primer (kg) | Powder (kg)
PRIMER PAINT & THINNER |  |  | 10 |  | 250 | 5 | 6 | 10 | 6
POWDER PAINT (RAL6028) Marine Grade |  |  | 6 |  | 800 | 10 | 15 | 20 | 15 |  | 10
INTERNAL PAINT |  |  | 10 |  | 1250 | 15 | 20 | 30 | 20
[5 empty] | 2000 | 20 | 30 | 40 | 30
Cooling Ducts |  |  |  |  | 2500 | 25 | 30 | 50 | 30
LV No. of Cooling Ducts | 0.33 |  |  |  | 3150 | 30 | 40 | 60 | 40
LV MTL | 607.171 |  |  |  | 4000 | 40 | 50 | 70 | 50
LV No. of Layers | 36 |  |  |  | 5000 | 50 | 60 | 80 | 60
LV Cooling duct height | 203
| 0.33 | 18 |  |  | 1/3 Cooling Duct Between Layers 18 & 19 (203 x 200 mm)
| 0.67 | 18 |  |  | 2/3 Cooling Duct Between Layers 18 & 19 (203 x 400 mm)
| 1 | 18 |  |  | Full Cooling Duct Between Layers 18 & 19 (203 x 610 mm)
| 1.33 | 15 | 25 |  | Full Cooling Duct Between Layers 15 & 16 (203 x 550 mm) | 1/3 Cooling Duct Between Layers 25 & 26 (203 x 220 mm)
| 1.67 | 13 | 24 |  | Full Cooling Duct Between Layers 13 & 14 (203 x 550 mm) | 2/3 Cooling Duct Between Layers 24 & 25 (203 x 450 mm)
| 2 | 12 | 24 |  | Full Cooling Duct Between Layers 12 & 13 (203 x 550 mm) | Full Cooling Duct Between Layers 24 & 25 (203 x 670 mm)
| 2.33 | 10 | 21 | 28 | Full Cooling Duct Between Layers 10 & 11 (203 x 520 mm) | Full Cooling Duct Between Layers 21 & 22 (203 x 610 mm) | 1/3 Cooling Duct Between Layers 28 & 29 (203 x 230 mm)
| 2.67 | 9 | 19 | 27 | Full Cooling Duct Between Layers 10 & 10 (203 x 520 mm) | Full Cooling Duct Between Layers 19 & 20 (203 x 610 mm) | 2/3 Cooling Duct Between Layers 27 & 28 (203 x 470 mm)
| 3 | 9 | 18 | 27 | Full Cooling Duct Between Layers 9 & 10 (203 x 520 mm) | Full Cooling Duct Between Layers 18 & 19 (203 x 610 mm) | Full Cooling Duct Between Layers 27 & 28 (203 x 700 mm)
HV No. of Cooling Ducts | 1
HV MTL | 876.5
HV No. of Layers | 31
HV Cooling duct height | 203
| 0.33 | 15 |  |  | 1/3 Cooling Duct Between Layers 15 & 16 (203 x 290 mm)
| 0.67 | 15 |  |  | 2/3 Cooling Duct Between Layers 15 & 16 (203 x 580 mm)
| 1 | 15 |  |  | Full Cooling Duct Between Layers 15 & 16 (203 x 880 mm)
| 1.33 | 13 | 22 |  | Full Cooling Duct Between Layers 13 & 14 (203 x 790 mm) | 1/3 Cooling Duct Between Layers 22 & 23 (203 x 320 mm)
| 1.67 | 11 | 21 |  | Full Cooling Duct Between Layers 11 & 12 (203 x 790 mm) | 2/3 Cooling Duct Between Layers 21 & 22 (203 x 640 mm)
| 2 | 10 | 20 |  | Full Cooling Duct Between Layers 10 & 11 (203 x 790 mm) | Full Cooling Duct Between Layers 20 & 21 (203 x 960 mm)
| 2.33 | 9 | 18 | 24 | Full Cooling Duct Between Layers 9 & 10 (203 x 750 mm) | Full Cooling Duct Between Layers 18 & 19 (203 x 880 mm) | 1/3 Cooling Duct Between Layers 24 & 25 (203 x 340 mm)
| 2.67 | 8 | 16 | 23 | Full Cooling Duct Between Layers 9 & 9 (203 x 750 mm) | Full Cooling Duct Between Layers 16 & 17 (203 x 880 mm) | 2/3 Cooling Duct Between Layers 23 & 24 (203 x 670 mm)
| 3 | 7 | 15 | 23 | Full Cooling Duct Between Layers 7 & 8 (203 x 750 mm) | Full Cooling Duct Between Layers 15 & 16 (203 x 880 mm) | Full Cooling Duct Between Layers 23 & 24 (203 x 1010 mm)
Note on D81: Eranga: VALUE(LEFT(P!C82,FIND(".",P!C82,1)-1))
Note on D82: Eranga: VALUE(LEFT(P!C83,FIND(".",P!C83,1)-1))
Note on B83: Eranga: =ROUNDUP(C79*100,2)
Note on B84: Eranga: =MROUND(D80*C80+2,5)
Note on B85: Eranga: =MROUND(D81*C81/B84+2,5)
Note on C140: Eranga Anuradha Bala: =IF(AND(B47<30000,B46<=400),B134-2,IF(VALUE(B134)<611,B134,MROUND(B134-3,5)))
Note on G153: Eranga: Double foil 0.15 DL x 2
Note on G211: Eranga: Axial Parallel

## Bill of Materials
Bill of Materials
Transformer Type: |  | 100kVA 33000/400V
Contract No.:
Customer: |  | Imperio
No of Transformers: |  | 73
| Material | Description | Unit | Qty | Unit Price | Cost | % | Total Quantity | Per Winding Quantity | LME (U$/MT) = 8500
| MAJOR MATERIALS |  |  | xxx
1 | Oil | Inhibited Mineral Oil | L | 339.0805 | 1.3 | 440.8046 | 10.12% | 24752.8736
2
LV Winding
3 | LV Conductor | 185 x 0.12 x 2 | kg | 26.09 | 9.86 | 257.2474 | 5.904% | 1904.57 | 8.6967
4 | Flat Copper | 3*25mm | kg | 2.77 | 10.51 | 29.1127 | 0.6681% | 202.21 | 0.92333
5 | DDP Double Layer | 203mm x 0.15 DDP DL | kg | 2.94 | 9.03 | 26.5482 | 0.6093% | 214.62 | 0.98
6 | DDP Single Layer | 203mm x 0.15 DDP SL | kg | 0 | 4.7 | 0 | 0% | 0 | 0
7 | DDP Single Layer | 203mm x 0.25 DDP SL | kg | 0 | 3.72 | 0 | 0% | 0 | 0
8 | LV Edge Strip | 8 x 0.25mm | kg | 0.22558 | 5.09 | 1.1482 | 0.02635% | 16.4671 | 0.075192
9 | LV Insulation Packet | 100/33 INLV | Nos. | 3 | 2 | 6 | 0.1377% | 219
10 | [5 empty] | 0 | 0% | 0
HV Winding
11 | HV Conductor | 0.700mm CU-Round | kg | 48.97 | 9.91 | 485.2927 | 11.14% | 3574.81 | 16.3233
12 | DDP Single Layer | 203mm x 0.15 DDP SL | kg | 0 | 4.7 | 0 | 0% | 0 | 0
13 | DDP Single Layer | 203mm x 0.25 DDP SL | kg | 2 | 4.48 | 8.96 | 0.2056% | 146 | 0.66667
14 | HV Strip Insulation | 33 x 0.05 mm Strip | kg | 11.0587 | 4.89 | 54.0772 | 1.241% | 807.2876 | 3.6862
15 | HV Edge Strip | 33 x 0.25mm | kg | 0 | 6.26 | 0 | 0% | 0 | 0
16 | HV Insulation Packet | 100/33 INHV | Nos. | 3 | 40.3 | 120.9 | 2.775% | 219
17
Assembly
18 | HD Copper | 3 mm | kg | 4 | 13.13 | 52.52 | 1.205% | 292
19 | Bare Copper | 7/1.7 mm | kg | 0 | 15.45 | 0 | 0% | 0
20 | Bare Copper | 19/1.35 mm | kg | 0 | 7.65 | 0 | 0% | 0
21 | Copper Flexible | 100/33 CUFX | Nos. | 4 | 4.52 | 18.08 | 0.4149% | 292
22 | Timber Packet | 100/33 TMBC & TMAS | Nos. | 1 | 28.31 | 28.31 | 0.6497% | 73
23 | Insulation Packet | 100/33 INBC & INAS | Nos. | 1 | 100.3 | 100.3 | 2.302% | 73
24 | Assembly Packets (Core+Tanking+Dispatch) |  | Nos. | 1 | 20 | 20 | 0.459% | 73
24 | Copper Assembly |  | kg | 2 | 11.32 | 22.64 | 0.5196% | 146
| CORE STEEL |  | kg | 338.1 | 3.97 | 1342.257 | 30.8% | 24681.3
21 | 23ZDKH85 | 130mm | kg | 156.8 |  | 0 | 0% | 11446.4
22 | 23ZDKH85 | 120mm | kg | 99.2 | 0 | 0 | 0% | 7241.6 |  | General Choice
23 | 23ZDKH85 | 100mm | kg | 52.5 | 0 | 0 | 0% | 3832.5 |  | #N/A | 100/33/400 EU CU | CU
24 | 23ZDKH85 | 70mm | kg | 29.6 | 0 | 0 | 0% | 2160.8
25 | 0 | 0 | kg | 0 | 0 | 0 | 0% | 0 |  | Custom Choice
26 | 0 | 0 | kg | 0 | 0 | 0 | 0% | 0
27 | 0 | 0 | kg | 0 | 0 | 0 | 0% | 0
28 | 0 | 0 | kg | 0 | 0 | 0 | 0% | 0
29 | 0 | 0 | kg | 0 | 0 | 0 | 0% | 0
| STEEL |  |  | xxx | [5 empty] | Special Requirements
30 | Tank Steel, Trava, Foot & Clamps |  | kg | 41 | 2.64 | 108.24 | 2.484% | 2993 |  | Cover Plate Thickness
31 | Fin Type Radiators | 100/33/400 Tank | kg | 197.2 | 3.48 | 686.256 | 15.75% | 14395.6 |  | Base Thickness
32 | Pole Mounting Bracket |  | Nos. |  |  | 0 | 0% | 0
33 | [9 empty] | Tank Wall Thickness
| ACCESSORIES |  |  | xxx
HV Bushings
33 | Plug-in Type 36 kV 250 A Interface B |  | Nos. | 3 | 44.21 | 132.63 | 3.044% | 219
34 | HV Cable Lugs |  | Nos. | 3 | 5 | 15 | 0.3442% | 219
| LV Bushings |  |  |  |  | 0 | 0%
35 | EN 250 |  | Nos. | 4 | 16.77 | 67.08 | 1.539% | 292
36 | LV Cable Lugs |  | Nos. | 4 | 8 | 32 | 0.7344% | 292
| Tap selector |  |  |  |  | 0 | 0%
37 | HR 7A3.335 (30kV 30A 100mm 5 Pos) |  | Nos. | 1 | 48.85 | 48.85 | 1.121% | 73
38
| Valves |  |  |  |  | 0 | 0%
39 | PRV T-10K1 1R" |  | Nos. | 1 | 9.19 | 9.19 | 0.2109% | 73
40 | PRV T-50 0.4 BAR |  | Nos. |  |  | 0 | 0% | 0
41 | DRAIN VALVE NW 22 |  | Nos. | 1 | 17.15 | 17.15 | 0.3936% | 73
42 | AIR RELEASE PLUG |  | Nos. |  |  | 0 | 0% | 0
43 | ARES DIN25 DOUBLE FLANGE GATE VALVE |  | Nos. |  |  | 0 | 0% | 0
44 | SINGLE FLANGE BALL VALVE 1" NW25S-SS |  | Nos. |  |  | 0 | 0% | 0
45 | THROTTLE VALVE FOR RADIATOR NW80 FORMB |  | Nos. | 0 |  | 0 | 0% | 0
46 | BALL VALVE 1" PELGER |  | Nos. | 0 |  | 0 | 0% | 0
47 | GATE VALVE WITH SAMPLING |  | Nos. |  | 165 | 0 | 0% | 0
48 | GATE VALVE WITHOUT SAMPLING |  | Nos. | 0 |  | 0 | 0% | 0
49 | SAMPLING VALVE |  | Nos. |  |  | 0 | 0% | 0
50 | BALL VALVE 1" Threaded on both sides |  | Nos. | 0 | 11 | 0 | 0% | 0
51 | [5 empty] | 0 | 0% | 0
| Oil Level Indicators |  |  |  |  | 0 | 0%
52 | Magnetic- with 400mm boss |  | Nos. | 0 |  | 0 | 0% | 0
53 | Magnetic- with 200mm boss |  | Nos. |  | 26.79 | 0 | 0% | 0
54 | 4 HOLES PRISMATIC |  | Nos. |  | 10.25 | 0 | 0% | 0
55 | 6 HOLES PRISMATIC |  | Nos. | 0 | 13.19 | 0 | 0% | 0
56 | 8 HOLES PRISMATIC |  | Nos. |  | 15.31 | 0 | 0% | 0
57 | FLOATING TYPE |  | Nos. | 1 | 7.07 | 7.07 | 0.1623% | 73
58 | VIAT SO4 - Dial Type with Contacts |  | Nos. | 0 | 120 | 0 | 0%
59 | VIAT SO6 - Dial Type with Contacts |  | Nos. |  | 158.13 | 0 | 0%
60 | [5 empty] | 0 | 0%
| Cable Boxes |  |  |  |  | 0 | 0%
61 | HV CABLE BOX |  | Nos. |  | 0 | 0 | 0% | 0
62 | LV CABLE BOX |  | Nos. | 0 | 800 | 0 | 0% | 0
63 | WTI BOX |  | Nos. |  | 0 | 0 | 0% | 0
64 | CONNECTOR BOX |  | Nos. | 0 | 155 | 0 | 0% | 0
65 | CT Terminal Box |  | Nos. | 0 | 60 | 0 | 0% | 0
66 | [5 empty] | 0 | 0% | 0
| Other Parts |  |  |  |  | 0 | 0%
67 | RATING PLATE |  | Nos. | 1 | 3.64 | 3.64 | 0.08354% | 73
68 | PHASE MARKING PLATES |  | Nos. | 1 | 1.52 | 1.52 | 0.03488% | 73
69 | S/A MOUNTING BRACKET A-2 |  | Nos. | 0 | 15.42 | 0 | 0% | 0
70 | ISD UNIT |  | Nos. | 0 | 274.96 | 0 | 0% | 0
71 | BREATHER 1KG TYPE A |  | Nos. | 0 | 17.37 | 0 | 0% | 0
72 | BREATHER 1KG TYPE B |  | Nos. | 0 | 25.19 | 0 | 0% | 0
73 | BREATHER 1KG TYPE C |  | Nos. | 0 | 18.6107 | 0 | 0% | 0
74 | BREATHER 2KG |  | Nos. | 0 |  | 0 | 0% | 0
75 | THERMOMETER TEK 16 |  | Nos. | 0 |  | 0 | 0% | 0
76 | THERMOWELL 3/4" BSP |  | Nos. | 0 | 5 | 0 | 0% | 0
77 | THERMOMETER POCKET |  | Nos. |  | 3 | 0 | 0% | 0
78 | GALVANIZED CUP FOR THERMOMETER POCKET |  | Nos. |  | 3 | 0 | 0% | 0
79 | BUCHOLZ RELAY EW712 |  | Nos. | 0 | 262.56 | 0 | 0% | 0
80 | CONSERVATOR FILLING CAP AL. 2" |  | Nos. | 0 | 9 | 0 | 0% | 0
81 | T/F WHEEL 7613T00691 |  | Nos. |  | 15 | 0 | 0% | 0
82 | T/F WHEEL 7613T00691 |  | Nos. |  |  | 0 | 0% | 0
83 | OIL TEMP. INDICATOR TD50 (354 01 12X6.0) |  | Nos. | 0 | 1100 | 0 | 0% | 0
84 | WINDING TEMP. INDICATOR TD76 (354 01 12X6.0) |  | Nos. | 0 | 1050 | 0 | 0% | 0
85 | RTD WTI (PT100) |  | Sets. |  |  | 0 | 0% | 0
86 | RTD OTI (PT100) |  | Sets. |  |  | 0 | 0% | 0
87 | CT 3000/2A Oil Immersed (Measuring) Ring Type 15VA/0.5 |  | Nos. | 0 | 90 | 0 | 0% | 0
88 | CT 5000/5A Oil Immersed (Measuring) Ring Type 15VA/0.5 |  | Nos. |  | 60 | 0 | 0% | 0
89 | CT 1600/1A 5P20 15VA/0.5 2 Core |  | Nos. | 0 | 180 | 0 | 0% | 0
90 | NCT 400/1A 5P20 15VA |  | Nos. |  | 235.305 | 0 | 0% | 0
91 | NCT 1600/1A 5P20 15VA |  | Nos. |  | 127.575 | 0 | 0% | 0
92 | NCT 2000/1A 5P20 15VA |  | Nos. |  | 297.675 | 0 | 0% | 0
93 | CT TERMINAL BOX (2 TERMINALS) |  | Nos. |  |  | 0 | 0% | 0
94 | CT TERMINAL BOX (4 TERMINALS) |  | Nos. |  | 50 | 0 | 0% | 0
95 | CT TERMINAL BOX (6 TERMINALS) |  | Nos. |  |  | 0 | 0% | 0
96 | 24kV ELBOW CONNECTOR SET (03) |  | Nos. | 0 |  | 0 | 0% | 0
97 | 36kV ELBOW CONNECTOR SET (03) |  | Nos. | 0 |  | 0 | 0% | 0
98 | 52kV ELBOW CONNECTOR SET (04) |  | Nos. | 0 |  | 0 | 0% | 0
99 | OBO SURGE ARRESTERS |  | Nos. | 0 |  | 0 | 0% | 0
100 | LTL Name Board |  | Nos. | 1 | 7.03 | 7.03 | 0.1613% | 73
101 | Nut, Bolt & 2 Washers (Galvanized) M10 x 40 mm |  | Nos. |  |  | 0 | 0% | 0
102 | Split washers for tank cover fixing |  | Nos. |  |  | 0 | 0% | 0
103 | M12 bolt, nut, spring washer & lock washer for earthing terminal |  | Nos. |  |  | 0 | 0% | 0
104 | Flange Gasket |  | Nos. |  | 10 | 0 | 0% | 0
105 | Wooden Pallete For Packing |  | Nos. |  | 12 | 0 | 0% | 0
105 | Surge Arresters |  | Nos. |  | 14 | 0 | 0% | 0
| Painting |  |  |  |  | 0 | 0%
106 | GALVANIZING |  | kg |  | 0.30843 | 0 | 0% | 0
107 | PRIMER PAINT & THINNER |  | kg |  | 9.2 | 0 | 0% | 0
108 | POWDER PAINT (RAL6028) Marine Grade |  | kg |  | 7.37 | 0 | 0% | 0
109 | INTERNAL PAINT |  | kg |  | 7.6837 | 0 | 0% | 0
| 0 |  |  | 0 |  | 0 | 0% | 0
| Major Material |  | $ | * * * |  | 3808.694 | 87.41% | 278034.6613
| Accessories |  | $ | * * * |  | 341.16 | 7.83% | 24904.68
| Miscellaneous |  | $ | * * * | 5% | 207.4927 | 4.762% | 15146.9671
| Total Materials |  | $ | * * * |  | 4357.3467 | #DIV/0! | 318086.3084
Design Engineer
-
Note on L45: Eranga: If different radiator is used, type it here.

## Radiator Choise
Standard Copper EU2021 Radiators | 1000/33/415 EU | 1000/33/415 EU Tank
| 1000/33/400 EU | 1250/33/415 EU Tank
| 1000/33/440 EU | 1250/33/415 EU Tank
| 1000/33/690 EU | 1250/33/415 EU Tank
| 1000/33/800 EU | 1250/33/415 EU Tank
| 1250/33/415 EU | 1250/33/415 EU Tank
| 1250/33/400 EU | 1250/33/400 EU Tank
| 1250/33/440 EU | 1250/33/400 EU Tank
| 1250/33/690 EU | 1250/33/400 EU Tank
| 1250/33/800 EU | 1250/33/400 EU Tank
| 1600/33/415 EU | 1600/33/400 EU Tank
| 1600/33/400 EU | 1600/33/400 EU Tank
| 1600/33/440 EU | 1600/33/400 EU Tank
| 1600/33/690 EU | 1600/33/400 EU Tank
| 1600/33/800 EU | 1600/33/400 EU Tank
| 2000/33/415 EU | 2000/33/400 EU Tank
| 2000/33/400 EU | 2000/33/400 EU Tank
| 2000/33/440 EU | 2000/33/400 EU Tank
| 2000/33/690 EU | 2000/33/400 EU Tank
| 2000/33/800 EU | 2000/33/400 EU Tank
| 2500/33/415 EU | 2500/33/400 EU Tank
| 2500/33/400 EU | 2500/33/400 EU Tank
| 2500/33/440 EU | 2500/33/400 EU Tank
| 2500/33/690 EU | 3150/33/415 EU Tank
| 2500/33/800 EU | 2500/33/400 EU Tank
| 3150/33/415 EU | 3150/33/415 EU Tank
| 3150/33/400 EU | 3150/33/415 EU Tank
| 3150/33/440 EU | 3150/33/415 EU Tank
| 3150/33/690 EU | 3150/33/415 EU Tank
| 3150/33/800 EU | 3150/33/415 EU Tank
Standard Aluminium EU2021 Radiators | 1000/33/415 EU AL | 1250/33/400 EU AL Tank
| 1000/33/400 EU AL | 1250/33/400 EU AL Tank
| 1000/33/440 EU AL | 1250/33/400 EU AL Tank
| 1000/33/690 EU AL | 1250/33/400 EU AL Tank
| 1000/33/800 EU AL | 1250/33/400 EU AL Tank
| 1250/33/415 EU AL | 1250/33/400 EU AL Tank
| 1250/33/400 EU AL | 1250/33/400 EU AL Tank
| 1250/33/440 EU AL | 1250/33/400 EU AL Tank
| 1250/33/690 EU AL | 1250/33/400 EU AL Tank
| 1250/33/800 EU AL | 1250/33/400 EU AL Tank
| 1600/33/415 EU AL | 2000/33/400 EU AL Tank
| 1600/33/400 EU AL | 2000/33/400 EU AL Tank
| 1600/33/440 EU AL | 2000/33/400 EU AL Tank
| 1600/33/690 EU AL | 2000/33/400 EU AL Tank
| 1600/33/800 EU AL | 2000/33/400 EU AL Tank
| 2000/33/415 EU AL | 2000/33/400 EU AL Tank
| 2000/33/400 EU AL | 2000/33/400 EU AL Tank
| 2000/33/440 EU AL | 2000/33/400 EU AL Tank
| 2000/33/690 EU AL | 2000/33/400 EU AL Tank
| 2000/33/800 EU AL | 2000/33/400 EU AL Tank
| 2500/33/415 EU AL | 2500/33/400 EU AL Tank
| 2500/33/400 EU AL | 2500/33/400 EU AL Tank
| 2500/33/440 EU AL | 2500/33/400 EU AL Tank
| 2500/33/690 EU AL | 3150/33/400 EU AL Tank
| 2500/33/800 EU AL | 2500/33/400 EU AL Tank
| 3150/33/415 EU AL | 3150/33/400 EU AL Tank
| 3150/33/400 EU AL | 3150/33/400 EU AL Tank
| 3150/33/440 EU AL | 3150/33/400 EU AL Tank
| 3150/33/690 EU AL | 3150/33/400 EU AL Tank
| 3150/33/800 EU AL | 3150/33/400 EU AL Tank
Standard CEB Cu EU2021 Radiators | 100/33/415 EU CU | 160/33/415 EU CU Tank
| 160/33/415 EU CU | 160/33/415 EU CU Tank
| 250/33/415 EU CU | 250/33/415 EU CU Tank
| 400/33/415 EU CU | 400/33/415 EU CU Tank
| 630/33/415 EU CU | 630/33/415 EU CU Tank
| 800/33/415 EU CU | 800/33/415 EU CU Tank
| 1000/33/415 EU CU | 1000/33/415 EU CU Tank
| 100/11/415 EU CU | 100/11/415 EU CU Tank
| 160/11/415 EU CU | 160/11/415 EU CU Tank
| 250/11/415 EU CU | 250/11/415 EU CU Tank
| 400/11/415 EU CU | 400/11/415 EU CU Tank
| 630/11/415 EU CU | 630/11/415 EU CU Tank
| 800/11/415 EU CU | 800/11/415 EU CU Tank
| 1000/11/415 EU CU | 1000/11/415 EU CU Tank

## Techspecs
LTL TRANSFORMERS (PVT) LTD FRM/CI/02
Transformer Technical Specifications
Customer | STI Holdings – Tanzania project
Project: | STI Holdings – Tanzania project
Contract/Quotation No. |  |  | Design No: | 500 11 400 |  |  | Date: | 2023-05-30
Basic Technical Features |  |  | Unit | Customer Requirements |  | Review by LTL |  | Remarks
1. Capacity |  |  | kVA | 100 |  | 100
2. No. of Units required |  |  | Nos. | 15 |  | 15
3. Frequency |  |  | Hz | 50 |  | 50
4. No. of Phases |  |  |  | 3 |  | 3
5. Primary Voltage |  |  | V | 33000 |  | 33000
6. Tappings |  | 1 |  |  |  | 5%
2 | [5 empty] | 2.5%
3 | [5 empty] | 0%
4 | [5 empty] | -2.5%
5 | [5 empty] | -5%
-
-
-
-
7. Secondary Voltage (No Load) |  |  | V | 400 |  | 400
8. Vector Symbol |  |  |  | Dyn11 |  | Dyn11
9. Lightning Impulse Withstand Voltage (Primary / Secondary) |  |  | kV |  |  | 170 / - |  |  |  |  | 33 kV | 0 | 200 / - | 70 / 3
10. Power Frequency Withstand Voltage (Primary / Secondary) |  |  | kV |  |  | 70 / 3 |  |  |  |  | 33 kV | 1 | 170 / - | 70 / 3
11. Conductor Material (Primary / Secondary) |  |  |  | Cu / Cu |  | Cu / Cu
12. Temp. Rise | Windings |  | °C |  |  | 60 |  |  |  |  | 11 kV | 0 | 95 / - | 28 / 3
| Top Oil |  | °C |  |  | 55 |  |  |  |  | 7.2 kV | 0 | 75 / - | 28 / 3
13. Efficiency at 100% load (P.F = 0.8) |  |  | % |  |  | 97.8151 |  |  |  |  | 7.2 kV | 0 | 60 / - | 20 / 3
14. Voltage regulation at 100% load (P.F = 0.8) |  |  | % |  |  | 3.9948 |  |  |  |  | Custom Choise
15. No Load current |  |  | % |  |  | 0.82 |  | IEC Tolerances Applicable
16. Method of cooling | [5 empty] | ONAN
17. No load loss |  |  | W |  |  | 227 |  | IEC Tolerances Applicable
18. Load loss |  |  | W |  |  | 2500 |  | IEC Tolerances Applicable
19. Impedance voltage |  |  | % |  |  | 4.3 |  | IEC Tolerances Applicable
20. Sound level |  |  | dB |  |  | 45
21. Dimensions
| Length |  | mm |  |  | 1555 |  | Approximately
| Width |  | mm |  |  | 921 |  | Approximately
| Height |  | mm |  |  | 1062 |  | Approximately
22.Total Weight |  |  | kg |  |  | 980 |  | Approximately
23.Oil Weight |  |  | kg |  |  | 300 |  | Approximately
24.Un-tanking Weight |  |  | kg |  |  | 490 |  | Approximately
25. Availabilty of Cable box in Primary side, Y/N | [5 empty] | N |  |  | Y
26. Availabilty of Cable box in Secondary side, Y/N | [5 empty] | N |  |  | N
27. Hermetically sealed/Conservator |  |  |  | Hermetically sealed |  | Hermetically sealed |  |  | Includes in ISD | Hermetically sealed |  | Galvanize
28. Painting Method, Galvanize/Marine paint/Powder | [5 empty] | Marine paint |  | C5 |  | Conservator |  | Marine paint
29. Unit Colour | [5 empty] | RAL6028 |  | Dark Green |  |  |  | Powder
30. Service conditions
| Max. ambient temp. |  | °C |  |  | 45
| Monthly average temp. |  | °C |  |  | 35
| Yearly average temp. |  | °C |  |  | 25
31. Altitude (Maximum) |  |  | m |  |  | 1000
32. Standard | [5 empty] | IEC60076:2011
33. Protection Available |  | 34. Remarks : K Factor is selected as 1
ISD (includes protection for oil level, oil temp.,pressure & gas ) | N
Oil Level Indicator | Y |  | Designation |  | Sig. |  |  | Date
Pressure Release Device (With Contacts) | Y | Designed by: | EE |  |  |  |  | 2023-05-30
Winding Temperature Indicator | Y | Reviewed by: | EE |  |  |  |  | 2023-05-30
Bi- Directional Rollers | Y | Approved by: | EE |  |  |  |  | 2023-05-30
Revision No.: 03/01-12-2015
Note on H42: Eranga: =Q!B114
Note on H43: Eranga: =Q!B115
Note on H44: Eranga: =Q!B116
Note on H45: Eranga: =Q!B117
Note on H46: Eranga: =Q!B118
Note on H47: Eranga: =Q!B120

## DDOS
LTL TRANSFORMERS (PVT.) LTD. FRM/DE/01
DESIGN DATA OUTPUT SHEET
CORE DETAIL |  | B (T) : 1.450 | L (mm) : 73 |  |  | WT. (Kg) |  | L | #REF! | #REF!
V/T : 6.415 | GRADE : 23ZDKH | C - C (mm) : 294 | W1 / W2 / W3 / W4 (mm) : 29.5 / 20 / 17.5 / 11 (HV) / 4 (LV) |  |  |  |  | W1 | #REF! | #REF!
AREA : 199.3 cm2 |  | W - H (mm) : 232 | A (mm) : 184 | H (mm) : 130 |  | 156.8
|  |  |  | T1 / T2 / T3 / T4 (mm) : 120 / 100 / 70 / 0 |  | 99.2 / 52.5 / 29.6 / 0
WINDING TYPE |  | LV |  |  | HV
VOLTS (L/PH) V |  | 400 / 230.94 |  |  | 33000 / 33000
CURRENT (L/PH) A |  | 144.338 / 144.338 |  |  | 1.75 / 1.01
CONNECTION |  | yn |  |  | D
TEST (PF / IMP.) kV |  | 3 / - |  |  | 70 / 200 |  |  |  | 70 / 200 | 33 kV
TURNS |  | 36 |  |  | 5401 / 5144 |  |  |  | 70 / 170 | 33 kV |  | L | 5144 | 5 | 12
LAYERS |  | 36 |  |  | 31 |  |  |  | 28 / 75 | 11 kV
TURNS / LAYER |  | 1 |  |  | 178.00/ 61.00 * |  |  |  | 20 / 60 | 7.2 kV
INSULATION |  | (2 x 0.15 SL x 203) DDP Between Layers |  |  | Start Thickness 0.375 mm & End Thickness 1.65 mm |  |  |  | 3 / - | LV
0.075 x 45 Strip
EDGE STRIP (mm) |  | 8 x 0.25mm |  |  | 0.075 x 45 Strip
COOLING DUCT |  | 2/3 Cooling Duct Between Layers 11 & 12 (668 x 294 mm x 2) |  |  | Full Cooling Duct Between Layers 6 & 7 (668 x 1249 mm)
-
COND. SIZE BARE (mm) |  | 185 x 0.12 x 2 |  |  | 0.700
COND SIZE COVD. (mm) |  | 185 x 0.12 x 2 |  |  | 0.775
COND. AREA (mm2) |  | 44.398 |  |  | 0.385
AMPS / mm2 |  | 3.251 |  |  | 2.625
LEAD SIZE (mm) |  | 25.000 / 3.000 |  |  | HD Copper - 3 mm dia paper covered |  | HD Copper - 3 mm dia paper covered
FLEXIBLE SIZE (mm) |  | 25.000 / 3.000 |  |  | HD Copper - 3 mm dia paper covered
RADIALS (mm) |  | 15.24/ 15.24/ 19.74 |  |  | 39.35/ 39.35/ 39.35 |  | 7/1.7 bare copper
I.D/O.D (mm) (without tolerance) |  | 181 x 264 / 230 x 337 |  |  | 266 x 373 / 356 x 473 |  | 19/1.35 bare copper | [7 empty] | 133 | 193.49
ELEC./WDG. LGTH. (mm) |  | 185 / 205.000 |  |  | 138.225 / 205.000 | [9 empty] | 205.49 | 270.48
EQ. MEAN DIAM. (mm) |  | 96.6343 |  |  | 139.4993 | [9 empty] | 163.49 | 272.182
MEAN TURN (m) |  | 607.171 |  |  | 876.5 | [9 empty] | 240.48 | 349.172
WEIGHT TOTAL (Kg) |  | 30.87 |  |  | 57.10 | [9 empty] | 4
RESIST / PH (Ohm) |  | 0.010324 @ 75 C |  |  | 245.6654 @ 75 C
I2R + DIR STRAY (W) |  | 715 |  |  | 752
BUSHING |  | EN 250 x 4 |  |  | Plug-in Type 36 kV 250 A Interface B x 3
CLEARANCES | CORE / LV : 1.50x 1.50x 7.00 mm |  | LV/HV : | 15.000 mm | HV/HV : 21.000 mm | YOKE/COVER/BASE : 240 / 70 mm
LV INNER TUBE | 1 mm PB (668 mm x 794 mm) |  | STICK BARRIER : | 18 mm (668 mm x 1098 mm)
[9 empty] | Total | Noinal | No. of tap pos | Deviation
TAP | TURNS | LOSSES | CALCULATED | GUARANTEED |  | WEIGHTS (Kg) |  |  | 5401 | 5144 | 5 | 128.5 | 4887 | 4 | 5
1 | 0 | CAPACITY (kVA) | 100 | 100 | LV CU | 26.09
2 | 4887 |  |  |  | HV CU | 48.97
3 | 5016 | CU LOSS (W) | 1560 @ 75 C | 1560 | CU LEAD / BUSBAR | 2.77
4 | 5144 | FE LOSS (W) | 227 | 227 | TOTAL CU | 77.83
5 | 5144 |  |  |  | CORE | 321.7
6 | 5273 | TOTAL LOSS (W) | 928 @ 75 C |  | LV INSULATION | 2.94
7 | 5401 | REACTANCE (%) | 4.215 |  | HV INSULATION | 7.82
8 |  | IMPEDANCE (%) | 4.78 | 4.78 | CORE AND WDGS | 414
9 |  | NO LOAD CURRENT (%) | 0.82 |  | OIL WEIGHT | 295
10 |  | T. RISE OIL (°C) | 31.7 | 55 | WEIGHT OF RADIATOR | 79
11 |  | T. RISE WDG. (°C) | 47.6 | 60 | TOTAL WEIGHT | 882 |  |  | 47.6 | 41.3
12 |  | X/R | 6 |  | EXPANSION OIL VOLUME | 6 L
TANK INSIDE | LENGTH (mm) : 1035 |  |  | WIDTH (mm) : | 481 | HEIGHT (mm) : 802
[5 empty] | CORRUG. L.S DEPTH (mm) : 210 | NO.: 12
HEIGHT OF RADIATOR : |  | 600 |  |  | CORRUG. S.S DEPTH (mm) : 50 | NO.: 5
NUMBER OF RADIATORS : |  |  | CENTER LENGTH OF THE RADIATOR (mm) :
NUMBER OF ELEMENTS PER RADIATOR : |  |  | TYPE OF RADIATOR : |  |  |  | CENTERED
OFF CENTERED
RATING DETAILS
kVA | 100 | VECTOR | Dyn11 | COOLING | ONAN | CONTINUOUS : Y
PHASE | 3 | Hz | 50 | VOLTAGE RATIO : 142.894 |  | TYPE OF UNIT : Hermetically sealed | Hermetically sealed
TAPPINGS ON HV |  | ABOVE NOMINAL : | 2 | IN STEPS OF : 2.5 %
|  | BELOW NOMINAL : | 2 | TAP CHANGER TYPE : HR 7A3.335 (30kV 30A 100mm 5 Pos)
SPECIAL ACCESSORIES: SAMB A-2 |  | / OLI / WTI
STANDARD : IEC 60076:2011
CUSTOMER | : STI Holdings – Tanzania project |  |  | DESIGNED | : | DATE :
DESIGN NO | : 500 11 400 |  |  | REVIEWED | : | DATE :
CONTRACT NO : | : |  |  | AUTHORIZED | : | DATE :
Revision:02/01-07-2009
ISD / HV Enclosure 36kV 250A Interface B Plug-in Type Bushings / LV DT3150 Cable Box (6 runs per phase & neutral)